INTERNATIONAL GREEN CONSTRUCTION CODE™

PUBLIC VERSION 1.0

First Printing

Publication Date: March 2010

COPYRIGHT © 2010

INTERNATIONAL CODE COUNCIL, INC.

With the Cooperating Sponsorship of

American Institute of Architects

ASTM International

ISBN: 978-1-58001-630-8

ALL RIGHTS RESERVED. This version of the International Green Construction Code™ is a copyrighted work owned by the International Code Council, Inc. Without advance written permission from the copyright owner, no part of this work may be reproduced, distributed or transmitted in any form or by any means, including, without limitation, electronic, optical or mechanical means (by way of example, and not limitation, photocopying or recording by or in an information storage retrieval system). For information on permission to copy material exceeding fair use, please contact: Publications, 4051 West Flossmoor Road, Country Club Hills, IL 60478. Phone 1-888-ICC-SAFE (422-7233).

Trademarks: “International Code Council,” the “International Code Council” logo and the “International Green Construction Code” are trademarks of the International Code Council, Inc.

PRINTED IN THE U.S.A.

PREFACE

Introduction

All levels of government and Building Safety Professionals recognize the need for a mandatory baseline of codes addressing green commercial construction, providing a framework linking sustainability with safety and performance. The International Green Construction Code™, in this Public Version 1.0, is designed to meet these needs through model code regulations that promote safe and sustainable construction in an integrated fashion with the ICC Family of Codes.

This comprehensive code establishes minimum regulations for buildings and systems using prescriptive and performance-related provisions, working as an overlay to the I-Codes. For example, the requirements of the 2012 International Energy Conservation Code are established as a baseline for the International Green Construction Code energy provisions which can be increased through the selection of “Jurisdictional Requirements” and “Project Electives.” It is founded on the principle that a model code must address the market segments beyond those captured by rating systems or other evaluation guides, and therefore, must be enforceable, useable, and adoptable.

The International Green Construction Code provides many benefits, among which is the model code development process that offers an international forum for building professionals to discuss the science and performance of buildings and systems. This forum provides an excellent arena to debate improvements to the ICC Family of Codes and Standards. The ICC system promotes the mission of the ICC and consistency in the application of codes worldwide.

Development

Public Version 1.0 of the International Green Construction Code was prepared in 2010 by the Sustainable Building Technology Committee (SBTC)  created by the ICC Board of Directors, with the American Institute of Architects and ASTM International as Cooperating Sponsors. The SBTC is a broad based committee (see page v) representing a balance of interests consistent with the ICC Governmental Consensus process and revised OMB Circular A-119 which establishes policies on Federal use and development of voluntary consensus codes and standards. The SBTC was composed of 28 individuals from public, private and nonprofit sectors with an expertise in disciplines critical to the topics in the International Green Construction Code. The SBTC was supported by several Work Groups composed of additional experts, along with a staff Secretariat and four staff experts. The intent was to develop a comprehensive set of regulations for green building systems consistent and coordinated with the I-Codes.

Technical content was developed from an initial staff resource document, which utilized approaches from the California Green Building Standards Code along with leading edge information from numerous other sources, as well as staff expertise. The SBTC and its Work Groups sought to refine initial conceptual positions articulated by the drafting participants into language that would be consistent with I-Code language and provide a basis for measuring green building performance. Consistent with the development of other I-Codes, the participants wrote the International Green Construction Code Public Version 1.0 with the intent to establish provisions consistent with the intent of the I-Codes to adequately protect public health, safety and welfare; provisions that do not unnecessarily increase construction costs; provisions that do not restrict the use of new materials, products or methods of construction; and provisions that do not give preferential treatment to particular types or classes of materials, products or methods of construction.

Public Meetings

In order to gain views of building safety professionals, industries, environmental interests and all other interested parties, five extensive public SBTC meetings were conducted (see the schedule on page xi). Changes to the text of the draft were accepted at the meetings of the full committee; changes to the text were also considered at the Work Group meetings prior to presentation to the full committee. An updated draft was posted on the ICC web site after every SBTC meeting which served as the baseline for the next period of Work Group meetings followed by consideration by the full committee. In addition to the changes made at each SBTC meeting, editorial changes have been made for consistency and correlation purposes.

Subsequent Versions

Public Version 2.0 will issue in November 2010 after the Public Comments submitted to Public Version 1.0 are considered at the Public Hearings in August/2010. Proposed revisions to Public Version 2.0 will be in the form of code changes which will be processed in accordance with ICC’s Code Development Process comprised of Code Development and Final Action Hearings in 2011, resulting in the 2012 International Green Construction Code.

Adoption

The International Green Construction Code Public Version 1.0 is available as a resource document to guide adoption and use by jurisdictions internationally. Its use within a governmental jurisdiction is intended to be accomplished through adoption by reference in accordance with proceedings establishing the jurisdiction's laws. At the time of adoption, jurisdictions should insert the appropriate information in provisions requiring specific local information, such as the name of the adopting jurisdiction. These locations are shown in bracketed words in small capital letters in the code and in the sample adoption ordinance. The sample adoption ordinance on page ix addresses several key elements of a code adoption ordinance, including the information required for insertion into the code text.

Maintenance

The International Green Construction Code will be kept up to date through the review of proposed changes submitted by code enforcement officials, industry representatives, design professionals and other interested parties. Proposed changes will be carefully considered through an open code development process in which all interested and affected parties may participate.

For more information regarding the code development process, contact: ICC at 4051 West Flossmoor Road, Country Club Hills, Illinois 60478;

While the development procedure of the International Green Construction Code assures the highest degree of care, the ICC, AIA, ASTM International and their members and those participating in the development of this code do not accept any liability resulting from compliance or noncompliance with the provisions given herein, for any restrictions imposed on materials or processes, or for the completeness of the text. ICC, AIA, and ASTM International do not have power or authority to police or enforce compliance with the contents of this code. Only the governmental body that enacts the code into law has such authority.

Letter Designations in Front of Section Numbers

In each code development cycle, proposed changes to the code are considered at the Code Development Hearings by the applicable ICC Code Development Committee, whose action constitutes a recommendation to the voting membership for final action on the proposed change. Proposed changes to a code section that has a number beginning with a letter in brackets are considered by a different code development committee. For example, proposed changes to code sections that have [B] in front of them (e.g., [B] 202 – definition of “Addition”) are considered by the ICC Building Code Development Committee at the code development hearings.

The content of sections in this code that begin with a letter designation are maintained by another code development committee in accordance with the following:

[E] = International Energy Conservation Code Development Committee;

[EB] = International Existing Building Code Development Committee;

[F] = International Fire Code Development Committee;

[FG] = International Fuel Gas Code Development;

[M] = International Mechanical Code Development; and

[P] = International Plumbing Code Development Committee

Developed by

Members of the Sustainable Building Technology Committee

Chair: Ravi Shah, ICC Board of Directors, Director of Urban Development, City of Carrolton, Texas

Vice Chair: Chris Green, AIA, LEED AP Representing AIA, President, AGO Studios, Inc., Avon, Colorado

Dennis A. Andrejko, FAIA

Representing AIA

Associate Professor of Architecture

University at Buffalo, Department of Architecture

Buffalo, NY

Jack Bailey, IES, LC, LEED AP

Representing International Association of Lighting Designers

Partner, One Lux Studio, LLC

New York, NY

Peter K. Bruck, LEED AP, MA

Sustainability Program Manager

U.S. General Services Administration - Region 10

Seattle, WA

David C. Conover

Senior Technical Advisor/S&E V

Pacific Northwest National Laboratory

Washington, DC

David Eisenberg

Executive Director

Development Center for Appropriate Technology

Tucson, AZ

Anthony C. Floyd, AIA, LEED AP

Green Building Program Manager

City of Scottsdale, AZ

Sam Francis

Northeast Regional Manager, Building Codes & Standards

American Forest & Paper Association

West Grove, PA

Holly Gerberding, FAIA

Coordinating Architect

Chicago Department of General Services

Chicago, IL

Josh R. Greenfield, PE, LEED AP

Senior Associate

Primera Engineers Ltd.

Chicago, IL

Maureen Guttman, AIA

Executive Director, Governor's Green Government Council

Pennsylvania Department of Environment Protection

Harrisburg, PA

Jonathan Humble, AIA, NCARB, LEED AP

Regional Director

American Iron and Steel Institute

West Hartford, CT

Ron Jones

Owner

Green Builder, LLC

Eastsound, WA

Stephen Kanipe, CBO, LEED AP

Chief Building Official

City of Aspen, CO

Medard Kopczynski, CBO

Assistant City Manager

City of Keene, NH

Carol Marriott, P. Eng.

Representing ASHRAE

Owner

Carol Marriott Consulting, LLC

Minneapolis, MN

R. Christopher Mathis, SMArchS

Representing ASTM International

President

M C 2 Mathis Consulting

Asheville, NC

Dennis McCabe

Superintendent of Building Department - Planning Director

Village of East Rockaway, NY

Ted Miltiades

Director, Office of Construction Codes

Georgia Department of Community Affairs

Atlanta, GA

Richard C. Morgan, PMP

Austin Energy Green Building Manager

Austin Energy/City of Austin, TX

Brendan Owens, PE, LEED AP

Vice President, LEED Technical Department

U.S. Green Building Council

Washington, DC

Stephen S. Szoke, PE

Director, Codes and Standards

Portland Cement Association

Skokie, IL

David Walls

Executive Director

California Building Standards Commission

Sacramento, CA

Robert Weber, PE, CBO

President

R. D. Weber & Associates, Inc.

Las Vegas, NV

Joseph D. Wendler, PE

Project Engineering Manager, Standards and Certification

American Society of Mechanical Engineers

New York, NY

Robert (Robin) White, LEED AP

Product Manager, Marketing Retail Sales and Development

Alabama Power Company

Birmingham, AL

A. Vernon Woodworth, AIA

Representing AIA

Associate Principal

R.W. Sullivan, Inc.

Boston, MA

Content Developed with the Research and Input of

Work Group Participants and Public Meeting Attendees, including

Accelerated Building Technologies, ACH&RI, Acuity Brands Lighting, Air-Conditioning Heating and Refrigeration Institute, AIA California Council, AIA COTE, AIA COTE Denver, AIA Illinois, AIA/State of Wisconsin, AIM LLC, Alliance for Water Efficiency, American Coatings Association, American Gas Association, American Rainwater Catchment Systems Association, American Society of Landscape Architects, American Society of Plumbing Engineers, American Wood Council, Anderson Corporation, Arby’s Restaurant Group, Arcon Services Inc., Asphalt Roofing Manufacturers Association, ASC, Association of Pool and Spa Professionals, American Society for Healthcare Engineering, Baltimore Air Coil, Barb Grady, BASF, Blue Ridge Atlantic Inc., Building Officials Association of Florida, Brick Industry Association, Broan/Nutone, Brown Chamblis, Building Quality, Cardinal Glass, California Department of Housing and Community Development, Caroma Dorg, CCCIA, CCICC, CES, Charlotte Pipe and Foundry, City of Golden, City of Houston, City of Southfield, City of Waco, Colorado Code Consulting LLC, Construction Testing and Engineering, Davidson Code Concepts/NASFM, DuPont, Edison Electric Institute, Energy Systems Lab-Texas A&M, EVAPCO, Fire Safety, Florida Natural Gas Association, Full Service Green, Gas Technology Institute, Georgia Pacific, Green Building Initiative, Greenguard, Gypsum Association, Hall-Woolford Tank Company, Hansgrohe Inc., Hearth Patio & BBQ Association/PFI, IAEI, Institute for Business and Home Safety, Institute for Market Transformation, Intech Consulting, Intercode Inc., International Association of Fire Chiefs, International Log Builders Association, Irrigation Association, ISO, Jay R. Smith Manufacturing Company, Jeld-Wen Inc., K. Hovnanian, The Kellen Company, Keystone DCM, Koch Hazard Associates, Lutron Electronics, Laclede Gas Company, Martin Hammer Architect, Masco, Masonry Alliance for Codes & Standards, Massachusetts Office of Energy and Environmental Affairs, Mathis Consulting, McKim and Creed Engineers PA, MMLP Ltd., National Association of Homebuilders, NAIMA, National Propane Gas Association, New Buildings Institute, NFSA, North Carolina Department of Environmental Resources, NOVA Chemicals, Obermayer Rebmann Maxwell & Hippel LLP, Osram Sylvania Lighting, Pacific Gas and Electric, Page Southerland Page, Piedmont Natural Gas, Plastics Piping Consultants, Plastic Pipe and Fittings Association, Plastic Pipe Institute, Plumbing Manufacturers Institute, PRB Connect, Rainfilters of Texas LLC, RCI Inc., Rainwater Management Solutions, Rocky Mountain Masonry Institute, Schneider Electric, SEDAC/BRC UIUC, Sheet Metal and Air-Conditioning Contractors National Association, Siemens, Spiezle Architecture Group, Single Ply Roofing Industry, Starbucks, Steel Framing Alliance, Tampa Bay Water, Target, Texas A&M University – College of Architecture, Texas Energy Systems Laboratory, Texas Legislative Service, The Athena Institute, The Green Building Initiative, The Preview Group, Tile Council of North America, TSA Codes & Standards Commission, Underwriters Laboratory, United Technologies Corporation (UTC- Carrier and UTC- Power), U.S. Environmental Protection Agency, U.S. General Services Administration, USG Corporation, U.S. Green Building Council, Uponor, Velux, Viega, Water Legacy LLC, Water Media Services, Watt Stopper, Window and Door Manufacturers Association

ICC Project Staff

Project Managers

Tom Frost, AIA — Senior Vice President

Mike Pfeiffer, PE — Deputy Senior Vice President

Staff Secretariats

Allan Bilka, RA — Senior Staff Architect

Gregg Gress — Senior Technical Staff

Darren Meyers, PE, CEM, GBE — Technical Director, Energy Programs

Kermit Robinson, CBO — Senior Technical Staff

Roadmap to the INTERNATIONAL GREEN CONSTRUCTION CODE

Chapter 3 is the core of the International Green Construction Code. It is formatted to: facilitate the customization of this code to address local issues; provide options for construction which exceed the minimum requirements of this code; and provide for the implementation of best practices. Table 302.1, which addresses jurisdictional choices, and Table 303.1, which introduces the concept of project electives, are fundamental to the understanding and use of this code.

Table 302.1 is designed to allow the local jurisdiction to meet regional goals and priorities by determining whether certain provisions are to be mandatory and whether enhanced energy performance or reduced plumbing fixture flow rates will be required for compliance with this code. This table also references ASHRAE 189.1 as a compliance path option. The determination of the minimum level of environmental performance for residential buildings regulated by the ICC 700 National Green Building Standard is included in this table as well.

Table 302.1 also requires that the local jurisdiction indicate a value between 0 and 14 as the minimum number of project electives that must be satisfied in order to comply with this code. Project electives are the vehicles by which this code encourages the consideration and implementation of environmentally beneficial practices that might not be appropriate as strict mandatory requirements in some scenarios. They are also used to encourage construction and performance which exceeds the minimum requirements of this code.

All of the provisions of this code, other than those selected by the jurisdiction in Table 302.1 and those designated as project electives, are mandatory as applicable. The section numbers listed in Table 302.1 become mandatory for all buildings in the jurisdiction only where the jurisdiction indicates such applicability in Table 302.1. Project electives, however, become mandatory only where they are selected or chosen by the owner or registered design professional and are indicated in Table 303.1, Project Electives Checklist. The primary functions of the checklist are to: a) give guidance to owners and design professionals as to what project electives are available to choose from, b) to inform the code official as to which project electives have been selected or chosen by the design professional and must, therefore, be complied with and enforced as if they were mandatory requirements and c) to encourage environmental performance that exceeds the minimum requirements of this code.

As an example, provisions of this code have been designated as project electives where mandatory compliance might not be feasible, but where that provision was, nonetheless, important to identify as an option from an environmental perspective. For example, it would be unreasonable to mandate that all buildings be constructed on a brownfield site, as that would preclude the construction of buildings on sites that were not brownfields. However, it is quite reasonable to allow the practice. Therefore, Section 407.2.4, which regulates brownfield sites, is designated as a project elective.

Buildings designed with higher energy performance or lower plumbing fixture flow rates than required by the jurisdiction in Table 302.1, or buildings that incorporate options, are credited with project electives in Table 303.1. Thus the concept of project electives facilitates the option of buildings performance that is higher than the minimum required by the International Green Construction Code.

Where a specific building project does not trigger the application of a mandatory provision, or where the jurisdiction has not selected a provision in Table 302.1 as mandatory in their jurisdiction, related project electives have been created to allow the implementation of the practice in those scenarios. For example, since Section 403.3, bicycle parking and storage, is not mandatory for buildings with an area of 25,000 square feet or less, the related project elective, Section 407.3.2, allows the application of the provision to smaller structures by allowing the design professional to select the provision as a project elective.

Provisions which are designated as project electives have been grouped in dedicated sections at the end of Chapters 4 through 9 so that they may be readily identified, and the Project Electives Checklist contained in Table 303.1 ties all project elective strategies from all chapters together in one location.

All sections which are not designated as jurisdictional choices in Table 302.1 or project electives in Table 303.1 are mandatory as applicable. This concept is reinforced in the general provisions at the beginning of Chapters 4 through 11. The vast majority of the provisions of this code are mandatory as applicable in the spirit of all other International Codes.

ORDINANCE

The International Codes are designed and promulgated to be adopted by reference by ordinance. Jurisdictions wishing to adopt the International Green Construction Code™ as an enforceable regulation governing structures and premises should ensure that certain factual information is included in the adopting ordinance at the time adoption is being considered by the appropriate governmental body. The following sample adoption ordinance addresses several key elements of a code adoption ordinance, including the information required for insertion into the code text.

SAMPLE ORDINANCE FOR ADOPTION OF

THE INTERNATIONAL GREEN CONSTRUCTION CODE

ORDINANCE NO.________

An ordinance of the [JURISDICTION] adopting the International Green Construction Code™, regulating and governing the impact of buildings and structures on the environment in the [JURISDICTION]; providing for the issuance of permits and collection of fees thereof; repealing Ordinance No. ______of the [JURISDICTION] and all other ordinances and parts of the ordinances in conflict therewith.

The [GOVERNING BODY] of the [JURISDICTION] does ordain as follows:

Section 1. That a certain document, three (3) copies of which are on file in the office of the [TITLE OF JURISDICTION’S KEEPER OF RECORDS] of [NAME OF JURISDICTION], being marked and designated as the International Green Construction Code, including Appendix Chapters [FILL IN THE APPENDIX CHAPTERS BEING ADOPTED] (see International Green Construction Code Section 101.2.1), as published by the International Code Council, be and is hereby adopted as the Green Construction Code of the [JURISDICTION], in the State of [STATE NAME] for regulating and governing the impact of buildings and structures on the environment as herein provided; providing for the issuance of permits and collection of fees thereof; and each and all of the regulations, provisions, penalties, conditions and terms of said Green Construction Code on file in the office of the [JURISDICTION] are hereby referred to, adopted, and made a part hereof, as if fully set out in this ordinance, with the additions, insertions, deletions and changes, if any, prescribed in Section 2 of this ordinance.

Section 2. The following sections are hereby revised:

Section 101.1. Insert: [NAME OF JURISDICTION]

Table 302.1. Insert: [JURISDICTIONAL REQUIREMENTS].

Section 3. That Ordinance No. ______ of [JURISDICTION] entitled [FILL IN HERE THE COMPLETE TITLE OF THE ORDINANCE OR ORDINANCES IN EFFECT AT THE PRESENT TIME SO THAT THEY WILL BE REPEALED BY DEFINITE MENTION] and all other ordinances or parts of ordinances in conflict herewith are hereby repealed.

Section 4. That if any section, subsection, sentence, clause or phrase of this ordinance is, for any reason, held to be unconstitutional, such decision shall not affect the validity of the remaining portions of this ordinance. The [GOVERNING BODY] hereby declares that it would have passed this ordinance, and each section, subsection, clause or phrase thereof, irrespective of the fact that any one or more sections, subsections, sentences, clauses and phrases be declared unconstitutional.

Section 5. That nothing in this ordinance or in the International Green Construction Code hereby adopted shall be construed to affect any suit or proceeding impending in any court, or any rights acquired, or liability incurred, or any cause or causes of action acquired or existing, under any act or ordinance hereby repealed as cited in Section 3 of this ordinance; nor shall any just or legal right or remedy of any character be lost, impaired or affected by this ordinance.

Section 6. That the [JURISDICTION’S KEEPER OF RECORDS] is hereby ordered and directed to cause this ordinance to be published. (An additional provision may be required to direct the number of times the ordinance is to be published and to specify that it is to be in a newspaper in general circulation. Posting may also be required.)

Section 7. That this ordinance and the rules, regulations, provisions, requirements, orders and matters established and adopted hereby shall take effect and be in full force and effect [TIME PERIOD] from and after the date of its final passage and adoption.

INTERNATIONAL GREEN CONSTRUCTION CODE SCHEDULE

The Sustainable Building Technology Committee (SBTC) completed Public Version 1.0 of the International Green Construction Code. The schedule includes the following steps:

| ACTIVITY | DATE |
| --- | --- |
| SBTC 1st Meeting | July 28 – 30, 2009; Rosemont, IL |
| SBTC 2nd Meeting | August 27 – 29, 2009; Denver, CO |
| SBTC 3rd Meeting | October 8 – 10, 2009; Philadelphia, PA |
| SBTC 4th Meeting | December 15 – 17, 2009; Fort Myers, FL |
| SBTC 5th Meeting | January 28 – 30, 2010; Austin, TX |
| Public Version 1.0 posted for comments (comment form on page xii) | March 15, 2010 |
| Comment Deadline | May 14, 2010 |
| Comments Posted | July 2, 2010 |
| Public Hearing to consider comments | August 14 – 22, 2010; Chicago |
| Public Version 2.0 posted for code change submittals | November 3, 2010 |
| 2011 International Green Construction Code Change Submittal Deadline | January 3, 2011 |
| 2011 International Green Construction Code Development Hearing | May 16 – 22, 2011; Dallas |
| 2011 International Green Construction Code Final Action Hearing | November 3 – 6, 2011; Phoenix |
| Publish 2012 International Green Construction Code | Early 2012 |

For a detailed schedule, please visit:

http://www.iccsafe.org/cs/IGCC/Pages/PublicVersionDevelopment.aspx

# PUBLIC COMMENT FORM

# FOR PUBLIC COMMENTS TO PUBLIC VERSION 1.0 OF THE

# INTERNATIONAL GREEN CONSTRUCTION CODE

CLOSING DATE:  All Comments Must Be Received by May 14, 2010

The 2010 IGCC Public Comment Hearings are scheduled for

August 14 – 22, 2010, in Rosemont, IL

DOWNLOAD AN ELECTRONIC VERSION OF THIS FORM AT:

http://www.iccsafe.org/cs/IGCC/Pages/PublicVersionDevelopment.aspx

1)

| Name: | Date: |
| --- | --- |
| Jurisdiction/Company: |
| Submitted on Behalf of: |
| Address: |
| City: | State: | Zip Code: |
| Phone: | Ext. | Fax: |
| E-mail address: |

2)	Comments can be formatted as either general comments concerning issues related to Public Version 1.0 or comments  that include changes to the text in legislative format. (see #4 below)  Changes to the text  are preferred in order to allow the hearing committee to fully understand the implications of the comment.  Public Version 1.0 has been posted in Word for ease of use in developing text changes in legislative format.  Text changes to Public Version 1.0 that are not correctly based on Public Version 1.0 will not be considered as part of your comment.

3)	Copyright Release: All Public Comments are required to include a copyright release. The copyright release form is posted with the electronic version of this public comment form.

4)	Comments should be sent to the following office via regular mail or email.  An email submittal is preferred, including an attached file(s) in Word. The comment should be formatted in legislative text with strikeout and underlining such that the comment is of presentation quality and ready for posting.  DO NOT PROCESS YOUR COMMENT IN TRACK CHANGES. See page xiii for instructions.

# Please use a separate form for each comment which addresses unrelated subject matter.  The comments will be assembled in Section number order to facilitate the public hearing process.

Please check here if a separate graphic file is provided. □ Graphic materials (Graphs, maps, drawings, charts, photographs, etc.)  must be submitted as separate electronic files in .CDR, IA, TIF or .JPG format (300 DPI Minimum resolution; 600 DPI or more preferred) even though they may also be embedded in your Word submittal.

Send to:

International Code Council

Chicago District Office

Attn: Dynice Broadnax

4051 West Flossmoor Road

Country Club Hills. IL 60478- 5795

Fax: 708/799-0320

IGCCcomments@iccsafe.org

Note:  All comments received will receive an acknowledgment by approximately May 21, 2010.  Please contact the ICC staff listed above if you do not receive an acknowledgment by May 21, 2010.

COMMENT INSTRUCTIONS

Comments which include text changes in legislative format are preferred. Your comment should be compiled as a separate file, attached to an email. Use separate files for each comment which address unrelated subject matter.

COMMENT FORMATTING: At the beginning of each section, one of the following instruction lines are needed: •Revise as follows •Add new text as follows •Delete and substitute as follows •Delete without substitution The comment should be formatted in legislative text with strikeout and underlining such that the comment is of presentation quality and ready for posting. DO NOT PROCESS YOUR COMMENT IN TRACK CHANGES.

SUPPORTING INFORMATION: The following items should be included in your comment: 1.Clearly state the purpose of the comment (e.g., clarify Public Version 1.0; revise outdated material; substitute new or revised material for Public Version 1.0; add new requirements; delete current requirements, etc.) 2. Justify changing Public Version 1.0, stating why the proposed text is superior to the provisions of Public Version 1.0. Comments that add or delete requirements should be supported by a logical explanation which clearly shows why Public Version 1.0 provisions are in need of a revision and how such text revisions will improve the code. 3. Substantiate the proposed text revisions in the comment based on technical information and substantiation. The burden of providing substantiating material lies with the commenter. A minimum of two copies of all substantiating information (including proposed new referenced standards) shall be submitted. Additional copies may be requested for distribution to the hearing committee.

COMMENT EXAMPLE

Comment #:  (to be filled in by ICC)

Section: 102.1.2

Commenter: John Q. Public, P.E, Acme Green Buildings, representing himself

Revise as follows:

102.1.2 Innovative Approaches. It is intended that The provisions of this code are intended to provide flexibility to allow and encourage the use of innovative approaches, techniques and technology to achieve compliance with the intent of the code.

Reason: An editorial rearrangement of the sentence structure to clarify that while “flexibility” is indeed an important attribute of the IGCC, it need not be stated as a code requirement. The entire section addresses the flexible nature of the code by virtue of the innovative approaches being encouraged in this section.

Table of Contents

CHAPTER 1:  ADMINISTRATION

SECTION 101: GENERAL	1

SECTION 102: APPLICABILITY	1

SECTION 103: DUTIES AND POWERS OF THE CODE OFFICIAL	4

SECTION 104: CONSTRUCTION DOCUMENTS	4

SECTION 105: APPROVAL	5

SECTION 106: PERMITS	6

SECTION 107: FEES	6

SECTION 108: BOARD OF APPEALS	6

SECTION 109: CERTIFICATE OF OCCUPANCY	6

CHAPTER 2:   DEFINITIONS	7

SECTION 201: GENERAL	7

SECTION 202: DEFINITIONS	7

CHAPTER 3   JURISDICTIONAL REQUIREMENTS AND PROJECT ELECTIVES	21

SECTION 301: General	21

SECTION 302: jurisdictional requirements	21

SECTION 303: project electives	24

SECTION 304: whole building life cycle assesSment	26

CHAPTER 4:   SITE DEVELOPMENT AND LAND USE	29

SECTION 401: general	29

SECTION 402: PRESERVATION OF NATURAL RESOURCES	29

SECTION 403: Transportation impact	34

SECTION 404: HEAT ISLAND MITIGATION	36

SECTION 405: SITE LIGHTING	38

SECTION 406: DETAILED SITE DEVELOPMENT REQUIREMENTS	40

SECTION 407: project electives	47

CHAPTER 5:   MATERIAL RESOURCE CONSERVATION AND EFFICIENCY	51

SECTION 501: general	51

SECTION 502: MATERIAL AND waste management	51

SECTION 503: material SELECTION	52

SECTION 504: LAMPS	53

SECTION 505: SERVICE LIFE	54

SECTION 506: CONSTRUCTION PHASE MATERIAL STORAGE, HANDLING & MOISTURE CONTROL	54

SECTION 507: PROJECT electives	55

CHAPTER 6:   ENERGY CONSERVATION, EFFICIENCY AND ATMOSPHERIC QUALITY	57

SECTION 601: general	57

SECTION 602: energy performance, peak power and reduced co2e emissions	57

SECTION 603: ENERGY USE AND ATMOSPHERIC IMPACTS	58

SECTION 604: ENERGY METERING, MONITORING AND REPORTING	63

SECTION 605: AUTOMATED DEMAND RESPONSE (AUTO-DR) INFRASTRUCTURE	66

SECTION 606: BUILDING ENVELOPE SYSTEMS	68

SECTION 607: BUILDING MECHANICAL SYSTEMS	72

SECTION 608: BUILDING SERVICE WATER HEATING SYSTEMS	78

SECTION 609: BUILDING ELECTRICAL POWER AND LIGHTING SYSTEMS	81

SECTION 610: SPECIFIC APPLIANCES AND EQUIPMENT	86

SECTION 611: BUILDING RENEWABLE ENERGY SYSTEMS	88

SECTION 612: ENERGY SYSTEMS COMMISSIONING AND COMPLETION	91

SECTION 613: JURISDICTIONAL REQUIREMENTS & PROJECT ELECTIVES	95

CHAPTER 7:   WATER RESOURCE CONSERVATION AND EFFICIENCY	99

SECTION 701: GENERAL	99

SECTION 702:  FIXTURES, FITTINGS, EQUIPMENT AND APPLIANCES	99

SECTION 703:  HVAC SYSTEMS AND EQUIPMENT	104

SECTION 704:  WATER TREATMENT DEVICES AND EQUIPMENT	104

SECTION 705:  SPECIFIC WATER CONSERVATION MEASURES	105

SECTION 706:  NON-POTABLE WATER REQUIREMENTS	105

SECTION 707:  RAINWATER COLLECTION AND DISTRIBUTION SYSTEMS	106

SECTION 708:  GRAYWATER SYSTEMS	114

SECTION 709:  RECLAIMED WATER SYSTEMS	120

SECTION 710:  PROJECT electives	122

CHAPTER 8:   INDOOR ENVIRONMENTAL QUALITY AND COMFORT	125

SECTION 801: GENERAL	125

SECTION 802: BUILDING CONSTRUCTION FEATURES, OPERATIONS AND MAINTENANCE FACILITATION	125

SECTION 803: HVAC SYSTEMS	125

SECTION 804: SPECIFIC indoor air quality & Pollutant Control MEASURES 	127

SECTION 805: ASBESTOS USE PREVENTION	133

SECTION 806: MATERIAL EMISSIONS & POLLUTANT CONTROL	134

SECTION 807: SOUND TRANSMISSION	138

SECTION 808: DAYLIGHTING	141

SECTION 809: PROJECT electives	143

CHAPTER 9:   COMMISSIONING, OPERATION AND MAINTENTANCE	145

SECTION 901: general	145

SECTION 902:  APPROVED AGENCY	145

SECTION 903:  COMMISSIONING	145

SECTION 904:  bUILDING oPERATIONS, mAINTENANCE AND OWNER EDUCATION	150

CHAPTER 10:   EXISTING BUILDINGS	153

SECTION 1001: GENERAL	153

SECTION 1002: ADDITIONS	153

SECTION 1003: ALTERATIONS TO EXISTING BUILDINGS	154

SECTION 1004: CHANGE OF OCCUPANCY	159

SECTION 1005: HISTORIC BUILDINGS	159

SECTION 1006: RELOCATED STRUCTURES	159

SECTION 1007: JURISDICTIONAL REQUIREMENTS	159

CHAPTER 11   EXISTING BUILDING SITE DEVELOPMENT	161

SECTION 1101: general	161

SECTION 1102: ADDITIONS	162

SECTION 1103: ALTERATIONS TO EXISTING BUILDING SITES	162

SECTION 1104: CHANGE OF OCCUPANCY	163

SECTION 1105: HISTORIC BUILDING SITES	163

CHAPTER 12:   REFERENCED STANDARDS	165

APPENDIX A:   OPTIONAL ORDINANCE	173

APPENDIX B:   GREENHOUSE GAS REDUCTIONS IN EXISTING BUILDINGS	179

SECTION B101: general	179

SECTION B102: DEFINITIONS	179

SECTION B103: PHASES	180

SECTION B104:  GREENHOUSE GAS REDUCTION METHODS	181

SECTION B105:  REFERENCED STANDARDS	181

APPENDIX C:   SUSTAINABILITY MEASURES	183

SECTION C101: general	183

SECTION C102: EFFICIENCY AND SUSTAINABILITY MEASURES	183

SECTION C103:  REFERENCED STANDARDS	186

APPENDIX D:   ENFORCEMENT PROCEDURES	187

SECTION d101: general	187

SECTION d102: APPLICABILITY	187

SECTION d103: DEFINITIONS	188

SECTION d104: DUTIES AND POWERS OF THE CODE OFFICIAL	188

SECTION D105: VIOLATIONS	188

SECTION d106: NOTICES AND ORDERS	189

SECTION d107: EMERGENCY MEASURES AND ABATEMENT	190

SECTION D108: MEANS OF APPEAL	191

Chapter 1

administration

PART 1 --- SCOPE AND APPLICATION

SECTION 101

GENERAL

101.1 Title. These regulations shall be known as the Green Construction Code of [NAME OF JURISDICTION], hereinafter referred to as “this code.”

101.2 Scope. The provisions of this code shall apply to the design, construction, addition, alteration, change of occupancy, movement, enlargement, replacement, repair, equipment, location, maintenance, removal and demolition of every building or structure or any appurtenances connected or attached to such buildings or structures and to the site on which the building is located . Occupancy classifications shall be determined in accordance with the International Building Code;

This code shall not apply to the following:

- Any Group R, Residential occupancies except as provided for in Section 102.4.12.

2.  Equipment or systems that are used primarily for industrial or manufacturing processes, except as otherwise provided in this code.

101.2.1 Appendices. Provisions in the appendices shall not apply unless specifically adopted.

101.3 Intent. The purpose of this code is to safeguard the environment, public health, safety and general welfare through the establishment of requirements to reduce the negative potential impacts and increase the positive potential impacts of the built environment on the natural environment and building occupants, by means of minimum requirements related to: conservation of natural resources, materials and energy; the employment of renewable energy technologies, indoor and outdoor air quality; and building operations and maintenance.

SECTION 102

APPLICABILITY

102.1 General. This code is an overlay to the other International Codes.  This code is not intended to be used as a stand alone construction regulation document or to abridge or supersede safety, health or environmental requirements under other applicable codes or ordinances.  A jurisdiction intending to adopt this code without other ICC-Codes is advised to make a detailed review of locally adopted codes to ensure that they adequately correlate with this code.

102.1.1 Code Conflicts. Where there is a conflict between a general requirement and a specific requirement of this code, the specific requirement shall be applicable. Where, in any specific case, different sections of the code specify different materials, methods of construction or other requirements, the most practical and effective requirement to meet the intent of the code shall govern.

102.1.2 Innovative Approaches. It is intended that the provisions of this code provide flexibility to allow and encourage the use of innovative approaches, techniques and technology to achieve compliance with the intent of the code.

102.2 Other laws. The provisions of this code shall not be deemed to nullify any provisions of local, state or federal law.

102.3 Application of references. References to chapter or section numbers, or to provisions not specifically identified by number, shall be construed to refer to such chapter, section or provision of this code.

102.4 Referenced codes and standards. The codes listed in Sections 102.4.1 through 102.4.12, the codes and standards referenced elsewhere in this code, and those referenced standards listed in Chapter 12, shall be considered as part of the requirements of this code to the prescribed extent of each such reference. It is the expressed intent of this code to require higher minimum standards relating to building performance than the corresponding minimum standards set by the referenced codes and standards, and in such cases, the higher minimum standards of this code shall take precedence.

102.4.1 Building. The provisions of the International Building Code shall apply to the extent that such provisions establish minimum requirements to safeguard public health, safety and general welfare through structural strength, means of egress facilities, sanitation, adequate light and ventilation, and safety to life and property from fire and other hazards attributed to the built environment and to provide safety to fire fighters and emergency responders during emergency operations. The provisions of Chapter 1 of the International Building Code shall also apply.

102.4.2 Fuel Gas. The provisions of the International Fuel Gas Code shall apply to the installation, alteration, repair and replacement of gas piping systems and components, gas appliances and related accessories as covered in this code. These requirements apply to gas piping systems extending from the point of delivery to the inlet connections of appliances and the installation and operation of gas appliances and related accessories.

102.4.3 Mechanical. The provisions of the International Mechanical Code shall apply to the installation, alterations, repairs and replacement of mechanical systems, equipment, appliances, fixtures, fittings and appurtenances, including ventilating, heating, cooling, air-conditioning and refrigeration systems, incinerators and other energy-related systems.

102.4.4 Plumbing. The provisions of the International Plumbing Code shall apply to the installation, alteration, repair and replacement of plumbing systems, including equipment, appliances, fixtures, fittings, appurtenances, and medical gas systems.

102.4.5 Property maintenance. The provisions of the International Property Maintenance Code shall apply to existing structures and premises; equipment and facilities; light, ventilation, space heating, sanitation, life and fire safety hazards; responsibilities of owners, operators and occupants; and occupancy of existing premises and structures.

102.4.6 Fire prevention. The provisions of the International Fire Code shall apply to matters affecting or relating to: structures, processes and premises from the hazard of fire and explosion arising from the storage, handling or use of structures, materials or devices; conditions hazardous to life, property or public welfare in the occupancy of structures or premises; and the construction, extension, repair, alteration or removal of fire suppression and alarm systems or fire hazards in the structure or on the premises from occupancy or operation.

102.4.7 Energy. The provisions of the International Energy Conservation Code shall apply to matters governing the design and construction of buildings for the effective use of energy.

102.4.8 Wildland-urban interface. The provisions of the International Wildland-Urban Interface Code shall apply to matters related to the mitigation of risk to life and structures from intrusion of fire from wildland fire exposures and fire exposures from adjacent structures and to mitigate structure fires from spreading to wildland fuels.

102.4.9 Performance. The provisions of the International Code Council Performance Code shall be permitted to apply to matters related to the approval of alternative materials and methods and to innovative approaches to code compliance.

102.4.10 Existing buildings. The provisions of the International Existing Building Code shall apply to matters governing the design and construction of additions, alterations or renovations of existing buildings as well as to changes in occupancy to the extent that such provisions establish minimum requirements to safeguard public health, safety and general welfare through structural strength, means of egress facilities sanitation, adequate light and ventilation, and safety to life and property from fire and other hazards attributed to the built environment and to provide safety to fire fighters and emergency responders during emergency operations.

102.4.11 Zoning. The provisions of the International Zoning Code shall apply to matters governing zoning requirements related to the scope of this code.

102.4.12 Residential occupancies. The provisions of ICC 700 are incorporated by reference and shall apply to the design and construction of buildings or portions thereof of Group R, including the building site. Such occupancies shall achieve the minimum environmental performance level as indicated in Table 302.1 in accordance with Section 303 of ICC 700 and as noted in Table 102.4.12. The minimum energy efficiency requirements shall be based on the performance path requirements of Table 102.4.12. Buildings of mixed use, one of which is Group R, shall comply with Section 102.4.12.1.

Exception: High-rise buildings as defined by the International Building Code shall comply with the provisions of this code or ICC 700.

TABLE 102.4.12

Residential Performance Requirements

| Residential coverage issue | ICC 700 Requirement |
| --- | --- |
| Environmental Performance Level | Bronze, Silver, Gold or Emerald in accordance with Table 303a |
| Minimum energy efficiency requirements – Performance Path | Mandatory requirements of Section 701. Performance path requirements in accordance with Section 701.1.1 that exceed the baseline minimum performance required by the 2006 IECC by 30 percent in accordance with 702.2 (2) and a minimum of two practices from Section 704. |

a. The environmental performance level in accordance with Table 303 of ICC 700 is to be determined by the jurisdiction.

102.4.12.1 Residential mixed use occupancies. The design and construction of residential portions of mixed use buildings shall comply with Section 102.4.12. The remainder of the building and the site on which the building is located shall comply with the provisions of this code. Where there are specific provisions provided in ICC 700 that regulate the design and construction of residential portions of the mixed occupancy, the provisions of ICC 700 shall apply.

Exception:  High-rise buildings as defined by the International Building Code shall comply with the provisions of this code or ICC 700.

102.5 Partial invalidity. In the event that any part or provision of this code is held to be illegal or void, this shall not have the effect of making void or illegal any of the other parts or provisions.

102.6 Existing structures. The legal occupancy of any structure existing on the date of adoption of this code shall be permitted to continue without change, except as is specifically covered in this code, the International Building Code, the International Existing Building Code, the International Property Maintenance Code or the International Fire Code, or as is deemed necessary by the code official for the general safety and welfare of building occupants and the public.

102.7 Mixed occupancy buildings. In mixed occupancy buildings, each portion of a building shall comply with the specific green construction requirements of this code which are applicable to each specific occupancy, except as provided in Section 102.4.12.

PART 2 --- ADMINISTRATION AND ENFORCEMENT

SECTION 103

DUTIES AND POWERS OF THE CODE OFFICIAL

103.1 General. The code official established in the International Building Code is hereby authorized and directed to enforce the provisions of this code. The code official shall have the authority to render interpretations of this code and to adopt policies and procedures in order to clarify the application of its provisions and how this code relates to other applicable codes and ordinances. Such interpretations, policies and procedures shall be in compliance with the intent and purpose of this code and other applicable codes and ordinances. Such policies and procedures shall not have the effect of waiving requirements specifically provided for in this code or other applicable codes and ordinances.

103.2 Applications and permits. The code official shall enforce compliance with the provisions of this code as part of the enforcement of other applicable codes and regulations, including the referenced codes listed in 102.4.

103.3 Notices and orders. The code official shall issue all necessary notices or orders to ensure compliance with this code.

103.4 Inspections. The code official shall make inspections, as required to determine code compliance, or the code official shall have the authority to accept reports of inspection by approved agencies or individuals. The code official is authorized to engage such expert opinion as deemed necessary to report upon unusual technical issues that arise, subject to the approval of the appointing authority.

SECTION 104

CONSTRUCTION DOCUMENTS

104.1  Information on construction documents. Construction documents shall be dimensioned and drawn upon suitable material. Electronic media documents are permitted to be submitted where approved by the code  official.  Construction documents shall be of sufficient clarity to indicate the location, nature and extent of the work proposed and show in detail that such work will conform to the provisions of this code and relevant laws, ordinances, rules and regulations, as determined by the code official. The construction documents shall contain a listing of the applicable project electives in accordance with Section 303, and shall include the applicable commissioning requirements in accordance with Section 903. Where special conditions exist, the code official is authorized to require additional construction documents.

SECTION 105

APPROVAL

105.1 General. This code is not intended to prevent the use of any material, method of construction, design, system, or innovative approach not specifically prescribed herein, provided that such construction, design, system or innovative approach has been approved by the code official as meeting the intent of this code and all other applicable laws, codes and ordinances.

105.2 Approved materials and equipment. Materials, equipment, devices and innovative approaches approved by the code official shall be constructed, installed and maintained in accordance with such approval.

105.2.1 Used materials and equipment. The use of used materials which meet the requirements of this code for new materials is permitted. Used equipment and devices shall not be reused unless tested to verify proper working condition and approved by the code official.

105.3 Modifications. Wherever there are practical difficulties involved in carrying out the provisions of this code, the code official shall have the authority to grant modifications for individual cases, upon application of the owner or owner’s representative, provided the code official shall first find that special individual reason makes the strict letter of this code impractical and that the modification is in compliance with the intent and purpose of this code and that such modification does not lessen the minimum requirements of this code. The details of granting modifications shall be recorded and entered in the files of the department.

105.4 Alternative materials, design, innovative approach and methods of construction and equipment. The provisions of this code are not intended to prevent the installation of any material or to prohibit any design, innovative approach, or method of construction not specifically prescribed by this code, provided that any such alternative has been approved. An alternative material, design, innovative approach or method of construction shall be reviewed and approved where the code official finds that the proposed design is satisfactory and complies with the intent of the provisions of this code, and that the material, design, method or work offered is, for the purpose intended, at least the equivalent of that prescribed in this code  The details of granting the use of alternative materials, designs, innovative approach and methods of construction shall be recorded and entered in the files of the department.

105.4.1 Research reports. Supporting data, where necessary to assist in the approval of materials or assemblies not specifically provided for in this code, shall consist of valid research reports from approved sources.

105.4.2 Tests. Wherever there is insufficient evidence of compliance with the provisions of this code, or evidence that a material or method does not conform to the requirements of this code, or in order to substantiate claims for alternative materials or methods, the code official shall have the authority to require tests as evidence of compliance to be made at no expense to the jurisdiction. Test methods shall be as specified in this code or by other recognized test standards. In the absence of recognized and accepted test methods, the code official shall approve the testing procedures. Tests shall be performed by an approved agency. Reports of such tests shall be retained by the code official for the period required for retention of public records.

105.5 Compliance materials. The code official shall be permitted to approve specific computer software, work- sheets, compliance manuals and other similar materials that meet the intent of this code.

SECTION 106

PERMITS

106.1 Required. Any owner or authorized agent who intends to construct, enlarge, alter, repair, move, demolish, or change the occupancy of a building or structure, or to erect, install, enlarge, alter, repair, remove, convert or replace any energy, electrical, gas, mechanical or plumbing system, the installation of which is regulated by this code, or to cause any such work to be done, shall first make application to the code official and obtain the required permit under the applicable code or regulation relevant to the intended work. Separate permits shall not be issued under this code. Exemptions from permit requirements shall not be deemed to grant authorization for any work to be done in any manner in violation of the provisions of this code or any other applicable laws, codes or ordinances of this jurisdiction.

SECTION 107

FEES

107.1 Fees.  Fees for permits shall be paid as required, in accordance with the schedule as established by the applicable governing authority for the intended work prescribed in an application.

SECTION 108

BOARD OF APPEALS

108.1 General. Appeals of orders, decisions or determinations made by the code official relative to the application and interpretation of this code shall be made to the Board of Appeals created under the applicable International Code of governing regulation.

108.2 Limitations on authority. An application for appeal shall be based on a claim that the true intent of this code or the rules legally adopted there under have been incorrectly interpreted, the provisions of this code do not fully apply or an equivalent or better form of construction is proposed. The board shall have no authority to waive requirements of this code.

108.3 Qualifications. The members of the board of appeals related to interpretation of this code shall be qualified by experience and training in the matters covered by this code and shall not be employees of the jurisdiction.

SECTION 109

CERTIFICATE OF OCCUPANCY

109.1 Use and occupancy. Buildings or structures shall not be used or occupied, and changes in the existing occupancy classification of a building or structure or portion thereof shall not be made, until the code official has issued a certificate of occupancy therefor as provided herein.  Issuance of a certificate of occupancy shall not be construed as an approval of a violation of the provisions of this code or of other ordinances of the jurisdiction.

109.2 Certificate issued. After the code official inspects the building or structure and finds no violations of the provisions of this code or other laws that are enforced by the department of building safety, the code official shall issue a certificate of occupancy in accordance with the provisions of the International Building Code.  The certificate of occupancy shall include a stipulation in accordance with Item 12 of Section 111.2 of the International Building Code that post occupancy requirements are to be completed in accordance with Chapter 9 of this code.

109.3 Temporary occupancy. The code official is authorized to issue a temporary certificate of occupancy before the completion of the entire work covered by the permit, provided that the building or structure or portion thereof is safe to occupy.

Chapter 2

DEFINITIONS

SECTION 201

GENERAL

201.1 Scope. Unless otherwise expressly stated, the following words and terms shall, for the purposes of this code, have the meanings shown in this chapter.

201.2 Interchangeability. Words used in the present tense include the future; words stated in the masculine gender include the feminine and neuter; the singular number includes the plural and the plural, the singular.

201.3 Terms defined in other codes. Where terms are not defined in this code and are defined in the International Building Code, International Energy Conservation Code, International Fire Code, International Fuel Gas Code, International Mechanical Code or International Plumbing Code, such terms shall have the meanings ascribed to them as in those codes.

201.4 Terms not defined. Where terms are not defined through the methods authorized by this section, such terms shall have ordinarily accepted meanings such as the context implies.

SECTION 202

DEFINITIONS

95th PERCENTILE RAINFALL EVENT.  The rainfall event where the amount of precipitation does not exceed 95 percent of all rainfall events during the period of record.

A-WEIGHTED SOUND LEVEL. Sound pressure level in decibels measured with a sound level meter using an A-weighted network.

[B] ADDITION. An extension or increase in floor area or height of a building or structure.

AGED SOLAR REFLECTANCE. The solar reflectance value of roofing after it has been installed and subjected to actual weather conditions for not less than three years.

[B] ALTERATION. Any construction or renovation to an existing structure other than repair or addition.

[B] APPROVED. Acceptable to the code official or authority having jurisdiction.

[B] APPROVED SOURCE. An independent person, firm or corporation, approved by the code official, who is competent and experienced in the application of engineering principles to materials, methods or systems analyses.

[B] APPROVED AGENCY. An established and recognized agency regularly engaged in conducting tests or furnishing commissioning services, where such agency has been approved.

AREA, TOTAL BUILDING FLOOR:  The total of the total floor areas on all stories of the building.

AREA, TOTAL FLOOR:  The total area of a story as measured from the interior side of the exterior walls.

AREA, OCCUPIED FLOOR:  The area of any story, portion of a story, or aggregate of multiple stories that is used for a specific occupancy or function.

[E] AUTOMATIC. Self-acting, operating by its own mechanism when actuated by some impersonal influence, such as a change in current strength, pressure, temperature or mechanical configuration (see “Manual”).

[P] BACKWATER VALVE. A device or valve installed in the system drain piping which prevents drainage or waste from backing up into the system and causing contamination or flooding.

BICYCLE PARKING, LONG TERM.  Bicycle racks or storage lockers provided for bicycle riders including, but not limited to, employees and students, anticipated to be at a building site for four or more hours.

BICYCLE PARKING, SHORT TERM.  Bicycle racks or storage lockers provided for bicycle riders including, but not limited to, customers, visitors, and event audiences, anticipated to be at a building site for less than four hours.

BIO-BASED MATERIAL. A commercial or industrial material or product, other than food or feed, that is composed of, or derived from, in whole or in significant part, biological products or renewable domestic agricultural materials, including plant, animal, and marine materials, or forestry materials.

BRANCH CIRCUIT. All circuit conductors between the final branch-circuit overcurrent device and the load.

[M] BTU. Abbreviation for British thermal unit, which is the quantity of heat required to raise the temperature of 1 pound (454 g) of water 1 F (0.56 C) (1 Btu = 1055 J).

[B] BUILDING. Any structure used or intended for supporting or sheltering any use or occupancy, including the energy using systems and site sub-systems powered through the building’s electrical service.

BUILDING COMMISSIONING (BCx) [See Code Change EC147-09/10]. A process that verifies and documents that the selected building systems have been designed, installed, and function according to the owner’s project requirements and construction documents, and to minimum code requirements except as noted herein.

BUILDING SITE.  A lot, or a combination of adjoining lots, that are being developed and maintained subject to the provisions of this code.  A building site shall be permitted to include public ways, private roadways, bikeways and pedestrian ways that are developed as an element of the total development.

[E] BUILDING THERMAL ENVELOPE. The basement walls, exterior walls, floor, roof, and any other building elements that enclose conditioned space. This boundary also includes the boundary between conditioned space and any exempt or unconditioned space.

CARBON DIOXIDE EQUIVALENT (CO2e) EMISSIONS. A measure used to compare the emissions from various greenhouse gases based upon their global warming potential (GWP).  CO2e emissions from carbon dioxide (CO2), methane (CH4), and nitrous oxide (N2O) are included. The carbon dioxide equivalent for a gas is derived by multiplying the weight of the gas by the associated GWP.

CHANGE OF OCCUPANCY.  A change in the purpose or level of activity within a building that involves a change in application of the requirements of this code.

CODE OFFICIAL. The officer or other designated authority charged with the administration and enforcement of this code, or a duly authorized representative.

COLLECTION PIPE. Unpressurized pipe used within the collection system that drains rainwater to the storage tank by gravity.

COMMERCIAL BUILDING. For this code, all buildings not included in the definition of residential building.

[as reconciled, pending IECC FAH, IgCC FAH, and CCC action] COMMISSIONING. A process that verifies and documents that the selected building and site systems have been designed, installed, and function in accordance with the owner’s project requirements and construction documents, and minimum code requirements.

CONSERVATION AREA.  Land designated by the jurisdiction, as a result of a community planning process, as appropriate for conservation from development due to the land possessing natural values important to the community including, but not limited to, wildlife habitat, forest or other significant vegetation, steep slopes, ground water recharge area, riparian corridor or wetland.

[B] CONSTRUCTION DOCUMENTS. Written, graphic and pictorial documents prepared or assembled for describing the design, location and physical characteristics of the elements of a project necessary for obtaining a building permit.

CONTROL. A specialized automatic or manual device or system used to regulate the operation of lighting, equipment or appliances.

DAYLIGHT CONTROL.  An automatic control device or system complying with Section 505.2.2.3.3 of the International Energy Conservation Code. [Section number based on change proposed for incorporation in the 2012 IECC]

CAPTIVE KEY CONTROL.  An automatic control device or system that energizes circuits when the key that unlocks the sleeping unit is inserted into the device and that de-energizes those circuits when the key is removed.

OCCUPANT SENSOR CONTROL.  An automatic control device or system complying with Section 505.2.2.3.1 of the International Energy Conservation Code. Occupant sensors are permitted to incorporate an integral maximum there (3) watt LED night light that functions when loads are shut off. [Section number based on change proposed for incorporation in the 2012 IECC]

TIME SWITCH CONTROL.  An automatic control device or system complying with Section 505.2.2.3.2 of the International Energy Conservation Code. [Section number based on change proposed for incorporation in the 2012 IECC]

CO2e. Weight of each gas emitted when consuming a specific energy type in the building per unit of the specific energy type provided to the building at the utility meter multiplied by the GWP of the specific gas, and then summed over all three gases emitted.

Where:

GWP (CO2) = 1

GWP (CH4) = 25

GWP (N2O) = 298.

[B] COURT. An open, uncovered space, unobstructed to the sky, bounded on three or more sides by exterior building walls or other enclosing devices.

DAYLIT AREA.  That portion of a building’s interior floor area that is regularly illuminated by natural light, as determined in accordance with Section 808.4.

DAYLIGHT SATURATION.   The percentage of daytime hours throughout the year when 30 foot-candles (323 lux) of natural light is provided at a height of 30 inches (762 mm) above the floor.  Partial credit is allowed for times when less than 30 foot-candles of natural light is provided.  Credit is not allowed for times when 450 foot-candles or more of natural light is provided.

DAYLIGHT ZONE, SIDELIGHTING.  The floor area adjacent to fenestration in an unobstructed exterior wall.  This area extends back from the exterior wall to the nearest 56 inch high partition, up to 2 times the height from the floor to the top of the fenestration, and laterally from the edge of the fenestration to the nearest 56 inch high partition, up to 0.5 times the height from the floor to the top of the fenestration.

DAYLIGHT ZONE, TOPLIGHTING.  The floor area beneath a skylight or monitor in an unobstructed roof. This area extends laterally and longitudinally beyond the edge of the skylight or monitor to the nearest 56 inch high partition, up to 0.7 times the height from the floor to the bottom of the skylight well.

Decibels (dB). Term used to identify ten times the common logarithm of the ratio of two like quantities proportional to the power of energy.

DECONSTRUCTION. The process of taking a building or structure apart, piece-by-piece, with the intent of recycling or salvaging as many of the materials and components as possible.

DEMAND LIMIT. The shedding of loads when pre-determined peak demand limits are about to be exceeded.

DEMAND RESPONSE, AUTOMATED (AUTO-DR). Fully Automated Demand Response initiated by a signal from a utility or other appropriate entity, providing fully-automated connectivity to customer energy end-use control strategies.

DEMAND RESPONSE AUTOMATION INTERNET SOFTWARE. Software that resides in a Building Energy Management Control System that can receive a demand response signal and automatically reduce HVAC and lighting system loads. Demand Response programs developed by the electric utility and the independent system operator typically depend upon timely and reliable communications of events and information to the buildings that are participating in the programs.

DETENTION. The short-term storage of stormwater on a site in order to regulate the runoff from a given rainfall event and to control discharge rates to reduce the impact on downstream stormwater systems.

DISTRIBUTION PIPE. Pressurized pipe used within the plumbing system of a building to deliver rainwater or graywater from the storage tank to the point of use.

DIVERSE USE CATEGORIES:   Categories of occupancies and land uses which are designated as either retail, service or community facilities:

Retail Uses:  The retail use category includes: Convenience store, florist, hardware store, pharmacy, grocery or supermarket and similar retail uses.

Service Uses:  The service use category includes:   Bank, coffee shop or restaurant; hair care; health club or fitness center; laundry or dry cleaner, medical or dental office and similar service uses.

Community Facilities:  The community facilities category includes:  Child care; civic or community center; a building containing a place of worship; police or fire station; post office, public library, public park, school, senior care facility, homeless shelter, and similar social services facilities.

[B] DWELLING UNIT. A single unit providing complete, independent living facilities for one or more persons, including permanent provisions for living, sleeping, eating, cooking and sanitation.

DRAIN TILE LOOP. A continuous length of drain tile or perforated pipe extending around all or part of the internal or external perimeter of a basement or crawl space footing.

EFFECTIVE APERTURE.  The effective aperture for vertical fenestration is the area of glazing in the unobstructed wall times the visible transmittance (VT) of this glazing, divided by the floor area in the daylight zone.  The effective aperture for skylights is the area of glazing in the unobstructed roof times the visible transmittance (VT) of this glazing, divided by the floor area in the daylight zone.

ENERGY MANAGEMENT AND CONTROL SYSTEM, BUILDING (EMCS). A computerized, intelligent network of electronic devices, designed to automatically monitor and control the energy using systems in a building.

ENERGY STAR. A joint program of the U.S. Environmental Protection Agency (EPA) and the U.S. Department of Energy (DOE) designed to identify and promote energy-efficient products and practices.

[M] equipment. All piping, ducts, vents, control devices and other components of systems other than appliances which are permanently installed and integrated to provide control of environmental conditions for buildings. This definition shall also include other systems specifically regulated in this code.

EQUIVALENT HEIGHT.  The continuous height, in vertical degrees, of an obstruction that provides the same obstructive effect as a series of obstructions of variable height. The line of equivalent height is drawn where the area of obstruction above equals the area of obstruction below. Determination shall be made on a floor by floor basis.

[B] EXISTING STRUCTURE. A structure erected prior to the date of adoption of the appropriate code, or one for which a legal building permit has been issued.

EXTERIOR WALL, FULLY OBSTRUCTED.  That portion of an exterior wall that does not face a public way or a yard or court complying with Section 1206 of the International Building Code.

EXTERIOR WALL, PARTIALLY OBSTRUCTED.  That portion of an exterior wall that is not a fully obstructed exterior wall, but which faces buildings, structures, or geological formations with an equivalent height more than 30 degrees above the horizon. For the purposes of this determination, the maximum allowed height of buildings or structures on adjacent property under existing zoning regulations is permitted to be considered.  Determination is  made on a floor by floor basis.

EXTERIOR WALL, UNOBSTRUCTED.  That portion of an exterior wall that is not an obstructed exterior wall, or a partially obstructed exterior wall.

FACILITY OPERATIONS.  A facility is operational during the time when the primary activity that facility is designed for is taking place.  For Group A and Group M occupancies, this is the time during which the facility is open to the public.

FARM LAND:

Prime farmland.  Land that has the best combination of physical and chemical characteristics for producing food, fiber, feed, forage, and oil seed crops and that is also available for these uses, including cropland, pastureland, forest land, range land and similar lands which are not water areas or urban or built-up land areas.

Unique farmland.  Land other than prime farmland that is used for the production of specific high-value food or fiber crops.  The land has the special combination of soil quality, location, growing season and moisture supply needed to economically produce sustained high-quality crops or high yields of a specific crop where the lands are treated and managed according to acceptable farming methods.

Farmlands of statewide significance.  Land, in addition to prime and unique farmlands, that is of statewide importance for the production of food, feed, fiber, forage and oil seed crops.  Criteria for delineating this land is determined by the appropriate state agency.

FEEDER CONDUCTORS.  The conductors that connect the service equipment to the branch circuit overcurrent devices.

[B] FIREPLACE. A hearth and fire chamber or similarly prepared place in which a fire can be made and that is built in conjunction with a chimney.

[B] FLOOD OR FLOODING.  A general and temporary condition of partial or complete inundation of normally dry land from:

1.	The overflow of inland or tidal waters.

2.	The unusual and rapid accumulation of runoff of surface waters from any source.

FLOOD HAZARD AREA. The greater of the following two areas:

- A floodplain;

- The area designated as a flood hazard area on a community’s flood hazard map, or otherwise legally designated.

FLOODPLAIN. The area of land which has a 1 percent or greater chance, in any year, of being inundated with water during high flows.  Floodplains are associated with both water courses such as rivers and streams and bodies of water such as oceans and lakes.

FREEBOARD.  Height above the base flood elevation of the lowest floor surface of any occupied portion of a building.

GLOBAL WARMING POTENTIAL. Global Warming Potentials (GWPs) are intended as a quantified measure of the globally averaged relative radiative forcing impacts of a particular CO2e. It is defined as the cumulative radiative forcing effects, both direct and indirect, of a gas integrated over a period of time from the emission of a unit mass of gas relative to some reference gas. Carbon dioxide (CO2) is the reference gas.

[P] GRAYWATER.  Untreated wastewater that has not come into contact with wastewater from water closets, urinals, kitchen sinks, or dishwashers. Graywater includes but is not limited to wastewater from bathtubs, showers, lavatories, clothes washers, and laundry trays.

GREENFIELD.  Land that has not been previously developed or has a history of only agricultural use.

GREENHOUSE GAS. A gas in the atmosphere that absorbs and emits radiation within the thermal infrared range.

HARDSCAPE. Areas of a building site covered by manmade materials.

HIGH OCCUPANCY VEHICLE.  A vehicle which is occupied by two or more people, when arriving and departing the site where parked, for not less than 75 percent of the vehicle trips; or as otherwise defined by state or local regulation.

[B] HISTORIC BUILDINGS. Buildings that are listed in or eligible for listing in the National Register of Historic Places, or designated as historic under an appropriate state or local law.

[B] HURRICANE-PRONE REGIONS. Areas vulnerable to hurricanes, defined as the U.S. Atlantic Ocean and Gulf of Mexico coasts where the basic wind speed is greater than 90 miles per hour (145 km/h), and Hawaii, Puerto Rico, Guam, Virgin Islands, and America Samoa.

INDEPENDENT SYSTEM OPERATOR (ISO). The electric system’s operator.

INFILL SITE.  Infill sites are one of the following:

- A vacant lot¸or collection of adjoining lots, located in an established, developed area that is already served by existing infrastructure;

- A previously developed lot which is being redeveloped.

INFRASTRUCTURE.  Facilities within a jurisdiction that provide community services and networks for travel and communication including: transportation services such as, but not limited to roads, bikeways and pedestrian ways and transit services; utility systems such as, but not limited to, water, sanitary sewage, stormwater management, telecommunications, power distribution and waste management; and community services such as, but not limited to, public safety, parks, schools and libraries.

infrastructure, Adequate.  The capacity of infrastructure systems, as determined by the jurisdiction, to serve the demands imposed by a new development on building sites within the jurisdiction.  Adequacy can be determined based on existing infrastructure or on the infrastructure as augmented by a development project.

INFRARED EMITTANCE. The ratio of radiant heat emitted by a sample to that emitted by a black body radiator at the same temperature.

INLET FILTER.  A screen, grid or other device installed on a gutter, downspout system or at another location upstream of the storage tank. The filter passes liquids and retains solids.

impervious surface.  Paved concrete or asphalt and other similar surfaces that readily accommodate the flow of water with relatively little absorption, as typically used at exterior horizontal areas including, but not limited to, parking lots, bikeways, walkways, plazas and fire lanes.

INVASIVE PLANT SPECIES:   A species that does not naturally occur in a specific area and the introduction of which causes or is likely to cause economic or environmental harm or harm to human health. Consideration for inclusion as on invasive species shall be permitted to include, but shall not be limited to, those species identified on:

- City, county or regional lists

- State Noxious Weeds laws,

- Federal Noxious Weeds laws.

[B] JURISDICTION. The governmental unit that has adopted this code under due legislative authority.

[B] LABEL. An identification applied on a product by the manufacturer that contains the name of the manufacturer, the function and performance characteristics of the product or material, and the name and identification of an approved agency and that indicates that the representative sample of the product or material has been tested and evaluated by an approved agency.

[B] LABELED. Equipment, materials or products to which has been affixed a label, seal, symbol or other identifying mark of a nationally recognized testing laboratory, inspection agency or other organization concerned with product evaluation that maintains periodic inspection of the production of the above-labeled items and whose labeling indicates either that the equipment, material or product meets identified standards or has been tested and found suitable for a specified purpose.

LIFE CYCLE ASSESSMENT. A technique to evaluate the relevant energy and material consumed and environmental emissions associated with the entire life of a building, product, process, activity or service.

LIGHTING BOUNDARY.  Where the lot line abuts a public walkway, bikeway, plaza, or parking lot, the lighting boundary shall be a line 5 feet from the lot line and located on the public property.  Where the lot line abuts a public roadway or public transit corridor, the lighting boundary shall be the centerline of the public roadway or public transit corridor.  In all other circumstances, the lighting boundary shall be at the lot line.

[B] LISTED. Equipment, materials, products or services included in a list published by an organization acceptable to the code official and concerned with evaluation of products or services that maintains periodic inspection of production of listed equipment or materials or periodic evaluation of services and whose listing states either that the equipment, material, product or service meets identified standards or has been tested and found suitable for a specified purpose.

[B] LOT. A portion or parcel of land considered as a unit.

[B] LOT LINE. A line dividing one lot from another, or from a street or any public place.

LOW EMISSION, HYBRID AND ELECTRIC VEHICLE.    Vehicles that achieve EPA Tier 2, California LEV-II, or a minimum of EPA LEV standards, whether by means of hybrid, alternative fuel, or electric power.

LOW VOLTAGE DRY-TYPE DISTRIBUTION TRANSFORMER. A NEMA ‘Class 1’ transformer that is air-cooled, does not use oil as a coolant, has an input voltage ≤ 600 Volts, and is rated for operation at a frequency of 60 Hertz.

[E] MANUAL. Capable of being operated by personal intervention (see “Automatic”).

MERV. Duct system air filter minimum efficiency reporting value.

METER.  A water volume measuring device used to collect data and indicate water usage abnormalities. Such devices are provided by the water purveyor or the building owner.

MUNICIPAL RECLAIMED WATER. Wastewater that has been reclaimed, recycled, reused or treated by a municipality for specific non-potable uses.

Noise. Any sound which is unnecessary, excessive, unnatural, annoying, prolonged, or unusually loud in relation to its time, place and use effect.

Non-potable water.  Water not safe for drinking, personal or culinary utilization.

OCCUPANT LOAD. The occupant load as calculated in accordance with the requirements of Chapter 10 of the International Building Code.

ORGANIC MATTER.  Soil carbon-containing material composed of both living organisms and formerly living, decomposing plant and animal matter. Soil organic matter content is either naturally occurring or is a result of supplementation with compost or other partially decomposed plant and animal material.

OUTLET FILTER. Devices that are located downstream of a storage tank and utilize screens, cartridges or other media to provide a level of filtration appropriate for the intended use of the water.

[B] PERMIT. An official document or certificate issued by the jurisdiction which authorizes performance of a specified activity.

POST-CONSUMER RECYCLED CONTENT. The proportion of recycled material in a product generated by households or by commercial, industrial, and institutional facilities in their role as end users of the product that can no longer be used for its intended purpose. This includes returns of material from the distribution chain.

potable water.  Water free from impurities present in amounts sufficient to cause disease or harmful physiological effects and conforming to the bacteriological and chemical quality requirements of the Public Health Service Drinking Water Standards or the regulations of the public health authority having jurisdiction.

POWER CONVERSION SYSTEM. The equipment used to convert incoming electrical power, to the force causing vertical motion of the elevator. In a traction system, this would include the electrical drive, motor, and transmission.

PRE-CONSUMER (POST-INDUSTRIAL) RECYCLED CONTENT. The proportion of recycled material in a product diverted from the waste stream during the manufacturing process. Pre-consumer recycled content does not include reutilization of material such as rework, regrind, or scrap generated in a process and capable of being reclaimed within the same process that generated it.

PROCESS LOADS. Building energy loads that are not related to building space conditioning, lighting, service water heating or ventilation for human comfort.

PROJECT ELECTIVE. The provisions contained in Sections 407, 507, 613, 710 and 809 for which compliance is not mandatory unless selected under Section 303.1 for a specific building project. The minimum total number of project electives that must be selected and complied with is indicated in Table 302.1.

PROPOSED DESIGN. A description of the proposed building used to estimate annual energy use for determining compliance based on total building performance including improvements in design such as the use of passive solar energy design concepts and technologies, improved building thermal envelope strategies, increased equipment and systems efficiency, increased use of daylighting, improved control strategies and improved lighting sources that will result in a decrease in annual energy.

[E] R-VALUE (THERMAL RESISTANCE). The inverse of the time rate of heat flow through a body from one of its bounding surfaces to the other surface for a unit temperature difference between the two surfaces, under steady state conditions, per unit area (h × ft2 × °F/Btu) [(m2 × K)/W].

RADON GAS. A naturally-occurring, chemically inert, radioactive gas that is not detectable by human senses. As a gas, it can move readily through particles of soil and rock and can accumulate under the slabs and foundations of homes where it can easily enter into the living space through construction cracks and openings.

RAINWATER.  Water from natural precipitation that was not contaminated by use.

RAINWATER COLLECTION AND CONVEYANCE SYSTEM. Rainwater collection system components extending between the collection surface and the storage tank that convey collected rainwater, usually through a gravity system.

REBOUND AVOIDANCE, SLOW RECOVERY. Slow recovery strategies slowly recover the target parameter that was controlled in the demand response strategy. Where this strategy is applied, the zone setpoints are gradually restored to the normal setpoints. Where air moving systems are targeted, a limit strategy is applied to the adjustable speed drive(s); fan adjustable speed drive limits are gradually shifted up.

REBOUND AVOIDANCE, SEQUENTIAL EQUIPMENT RECOVERY. Sequential equipment recovery that disperses short duration equipment start up spikes gradually, thereby avoiding a larger whole building demand spike.

REBOUND AVOIDANCE, EXTENDED AUTO-DR CONTROL. The rebound avoidance, extended Auto-DR control strategy is essentially an extension of the rebound avoidance, slow recovery strategy. Although a slow recovery strategy is critical to maximize the benefit of an Auto-DR strategy, the building energy management and control system (EMCS) programming for just such a strategy can be very complex or might not be possible for many conventional EMCS’s. A rebound avoidance, extended Auto-DR control strategy also includes logic and controls for avoiding a rebound peak when the control signal is stopped.

RECEIVING WATERS.  Groundwater, creeks, streams, rivers, lakes or other water bodies that receive treated or untreated wastewater or stormwater, including water from combined sewer systems and stormwater drains.

Reclaimed water.  Non-potable water that has been derived from the treatment of wastewater by a facility licensed or permitted to produce water meeting the jurisdiction’s water requirements for its intended uses.  Also known as “Recycled Water”

REGISTERED DESIGN PROFESSIONAL. An individual who is registered or licensed to practice their respective design profession as defined by the statutory requirements of the professional registration laws of the state or jurisdiction in which the project is to be constructed.

REGISTERED DESIGN PROFESSIONAL IN RESPONSIBLE CHARGE OF BUILDING ENERGY SIMULATION. A registered design professional responsible for the review and coordination of the building energy simulation documents and files of the project, as determined by the code official, for compatibility with the design and simulation of building components and energy-using systems of the building or structure, including submittal documents prepared by others, deferred submittal documents and phased submittal documents. This registered design professional is responsible for maintaining minimum competency in building energy simulation science in accordance with applicable certifications of minimum competence and nationally recognized standards as determined by the code official.

REGULARLY OCCUPIED SPACE.   A room or enclosed space which is regularly occupied for at least 1,000 daytime hours per year.  Restrooms, locker rooms, showers, changing rooms, closets, corridors, stairwells, mechanical and electrical equipment rooms are not considered to be regularly occupied.

RENEWABLE ENERGY SOURCE, ON-SITE.  Energy derived from solar radiation, wind, waves, tides, landfill gas, biomass, or the internal heat of the earth. The energy system providing on-site renewable energy is located on or adjacent to the building site, and generate energy for use on the building site.

RENEWABLE ENERGY CREDIT (REC). A REC represents the property rights to the environmental, social, and other non-power qualities of renewable electricity generation. A REC, and its associated attributes and benefits, is sold separately from the underlying physical electricity associated with an on-site renewable energy source. REC’s allow organizations to support renewable energy development and protect the environment where renewable power products are not locally available. There are two approaches to verifying REC ownership and the right to make environmental claims: (1) REC contracts including an audit of the chain of custody; and (2) REC tracking systems.

[B] REPAIR. The reconstruction or renewal of any part of an existing building for the purpose of its maintenance.

[E] RESIDENTIAL BUILDING. For energy purposes only, detached one- and two-family dwellings, and multiple single-family dwellings (townhouses), buildings under the scope of the International Residential Code, and Group R-2, R-3 and R-4 buildings, all of which are three stories or less in height above grade.

RETENTION (STORMWATER). The permanent holding of stormwater on a site, preventing the water from leaving the site as surface drainage and allowing for use of the water on site, or loss of the water through percolation, evaporation or absorption by vegetation.

ROOF COVERING. The covering applied to the roof deck for weather resistance, fire classification or appearance.

ROOF, FULLY OBSTRUCTED.  A roof that is below ground and covered by soil.

ROOF, PARTIALLY OBSTRUCTED.  That portion of the roof which is shaded by any building, structure, or geological formation at the peak solar altitude on the spring equinox, and three hours before and after the peak solar altitude on the spring equinox. For the purposes of this determination, the maximum allowed heights of buildings or structures on adjacent property under existing zoning regulations are permitted to be considered.

ROOF, UNOBSTRUCTED.  A roof that is not a fully obstructed roof or a partially obstructed roof.

ROOF WASHER. A device or method for removal of sediment and debris from collection surface by diverting initial rainfall from entry into the storage tank. Also referred to as a First Flush Device.

SEMI-HEATED SPACE. An enclosed space within a building that is heated by a heating system having an output capacity greater than or equal to 3.4 Btu/h·ft2 (1W/ft2; 10.8 W/m2) of floor area but less than 15 Btu/h·ft2 (4.4 W/ft2; 161.5 W/m2) of floor area.

SEQUENCE OF OPERATION (HVAC). Generated as a fully descriptive, detailed account of the operation of HVAC systems, the registered design professional describes the operation of systems in narrative terms accounting for all of the equipment that makes up the systems, how they are designed to operate, and how they are to be controlled. A sequence of operation is developed during the design process, and finalized upon commissioning, when the operational details are initialized and validated. A sequence of operation is the final record of system operation, and is included on the control diagram ‘as-builts’, or as part of the operation and maintenance (O&M) manuals that are turned over to the owner.

[B] SKYLIGHTS AND SLOPED GLAZING. Glass or other transparent or translucent glazing material installed at a slope of 15 degrees (0.26 rad) or more from vertical. Glazing material in skylights, including unit skylights, solariums, sunrooms, roofs and sloped walls, are included in this definition.

[B] SLEEPING UNIT. A room or space in which people sleep, that can also include permanent provisions for living, eating, and either sanitation or kitchen facilities but not both. Such rooms and spaces that are also part of a dwelling unit are not sleeping units.

SOIL-GAS-RETARDER. A continuous membrane of 6-mil (0.15 mm) polyethylene or other equivalent material used to retard the flow of soil gases into a building.

SOLAR INSOLATION. A measure of solar radiation energy received on a given surface area in a given time, expressed as average irradiance in kilowatt-hours per square meter per day (kW·h/(m2·day).

SOLAR PHOTOVOLTAIC EQUIPMENT. Devices such as solar cells and inverters that are used to transform solar radiation into energy.

SOLAR REFLECTANCE. A measure of the ability of a surface material to reflect sunlight. It is the fraction of solar flux, including the visible, infrared and ultraviolet wavelengths, reflected by a surface, expressed as a percentage on a scale of 0 to 1. Solar reflectance is also referred to as "albedo."

SOLAR REFLECTANCE INDEX (SRI).  A value that incorporates both solar reflectance and infrared emittance in a single measure to represent a material's temperature in the sun. SRI quantifies how hot a surface would get relative to standard black and standard white surfaces. SRI is calculated using equations based on previously measured values of solar reflectance and infrared emittance as laid out in ASTM E1980. SRI is expressed as a fraction, 0.0 to 1.0, or percentage, 0 percent to 100 percent.

SOLAR THERMAL EQUIPMENT. A device that uses solar radiation to heat water or air for use within the facility for service water heating, space heating or space cooling.

[E] STANDARD REFERENCE DESIGN. A version of the proposed design that meets the minimum requirements of the International Energy Conservation Code and the additional requirements of Table 603.3, and that is used to determine the maximum annual energy use for compliance based on total building performance.

STANDBY MODE (ELEVATOR). An operating mode during periods of inactivity in which electrical loads are reduced to conserve energy.  For elevators, standby mode begins up to 5 minutes after an elevator is unoccupied and has parked and completed its last run and ends when the doors are re-opened.  For escalators and moving walkways, standby mode begins after traffic has been absent for up to 5 minutes and ends when the next passenger arrives.

STORAGE TANK (GRAYWATER OR RAINWATER).  A fixed container for holding water at atmospheric pressure for subsequent reuse as part of a plumbing system.

[B] STORY. That portion of a building included between the upper surface of a floor and the upper surface of the floor or roof next above. It is measured as the vertical distance from top to top of two successive tiers of beams or finished floor surfaces and, for the topmost story, from the top of the floor finish to the top of the ceiling joists or, where there is not a ceiling, to the top of the roof rafters.

[B] STRUCTURE. That which is built or constructed.

SUBSLAB DEPRESSURIZATION SYSTEM (Passive). A system designed to achieve lower sub-slab air pressure relative to indoor air pressure by use of a vent pipe routed through the conditioned space of a building and connecting the sub-slab area with outdoor air, thereby relying on the convective flow of air upward in the vent to draw air from beneath the slab. 

SUBSLAB DEPRESSURIZATION SYSTEM (Active). A system designed to achieve lower sub-slab air pressure relative to indoor air pressure by use of a fan-powered vent drawing air from beneath the slab.

SUBMEMBRANE DEPRESSURIZATION SYSTEM. A system designed to achieve lower-sub-membrane air pressure relative to crawl space air pressure by use of a vent drawing air from beneath the soil-gas-retarder membrane.

TERTIARY STANDARDS. Standards, practices or policies that ensure that waste water has been treated to achieve a level of quality that is safe for release into the environment, such as, but not limited to, release into seas, rivers, lakes and the ground.

TOPSOIL.  The upper, outmost layer of soil having the highest concentration of organic matter and microorganisms and where the majority of biological soil activity occurs.

TOTAL ANNUAL NET ENERGY USE (TANEU). A ratio representing the energy performance of the proposed design compared to the energy performance of a standard reference design.  It is determined in accordance with Equation 6-2.

TRACTION ELEVATOR. An elevator system in which the cars are suspended by ropes wrapped around a sheave that is driven by an electric motor.

TRANSIT SERVICE.  A service that a public transit agency serving the area has committed to provide including, but not limited to, bus, streetcar, light or heavy rail, passenger ferry or tram service.

[E] U-FACTOR (THERMAL TRANSMITTANCE). The coefficient of heat transmission (air to air) through a building component or assembly, equal to the time rate of heat flow per unit area and unit temperature difference between the warm side and cold side air films (Btu/h · ft2  ·°F) [W/(m2 · K)].

VEGETATIVE ROOF:

Extensive vegetative roof.  A low profile roof with a growing medium less than 8 inches in depth, composed of plants that can thrive in a rooftop environment with limited water, shallow roots and sparse nutrients.

Intensive vegetative roof.  A high profile roof with a growing medium 8 inches or more in depth that can support a wide range of vegetables, shrubs and small trees.

[B] VENTILATION. The natural or mechanical process of supplying conditioned or unconditioned air to, or removing such air from, any space.

VOLATILE ORGANIC COMPOUND (VOC).  A chemical compound based on carbon chains or rings with vapor pressures greater than 0.1 millimeters of mercury at room temperature that typically contains hydrogen and sometimes contain oxygen, nitrogen and other elements.

VOCs, TOTAL (TVOCs). Sum of the concentrations of all identified and unidentified volatile organic compounds between and including n-pentane through n-heptadecane (i.e., C5 – C17) as measured by Gas chromatography/mass spectrometry total ion-current chromatogram method and expressed as a hydrocarbon equivalent value.

VOLTAGE DROP.  A decrease in voltage caused by losses in the circuit conductors connecting the power source to the load.

WASTE ENERGY RECOVERY. The application and use of systems and equipment to capture and reuse any form of energy that would otherwise be discarded and not otherwise be used by the building and its systems.

WETLAND.  Areas that are inundated or saturated by surface or groundwater at a frequency and duration sufficient to support, and that under normal circumstances do support, a prevalence of vegetation typically adapted for life in saturated soil conditions.

WIND POWER CLASS. As a renewable energy source, wind is classified according to wind power classes, based on typical wind speeds. These classes range from Class 1 (the lowest) to Class 7 (the highest). At the 50 meter (164 ft.) height, wind power Classes 4 and higher are considered good for development.

Chapter 3

jurisdictional requirements and PROJECT electives

SECTION 301

General

301.1 Scope. This chapter contains: requirements that are specific to and selected by the jurisdiction; elective requirements that are specific to the project and selected by the owner or registered design professional; and provisions for whole-building life-cycle assessment.

301.2 Mandatory and elective requirements. This chapter requires that the jurisdiction indicate in Table 302.1 whether specific provisions are mandatory for all buildings regulated by this code and, where applicable, the level of compliance required.  This chapter also contains project electives, as listed in Table 303.1, that become mandatory only as selected and indicated by the owner or registered design professional for the specific project. All other provisions of this code shall be mandatory as applicable.

SECTION 302

jurisdictional requirements

302.1 Requirements determined by the jurisdiction. The jurisdiction shall indicate the following information in Table 302.1 for inclusion in its code adopting ordinance:

- In accordance with Section 102.4.12, the jurisdiction shall indicate Bronze, Silver, Gold or Emerald as the minimum ICC 700 Environmental Performance Level for residential occupancies not regulated by this code by checking the corresponding box in Table 302.1. The minimum energy efficiency requirements shall be in accordance with Section 102.14.2. For residential mixed use occupancies, see Section 102.4.12.1.

- The jurisdiction shall indicate whether ASHRAE 189.1 is applicable by selecting “Yes” or “No” in the optional compliance path in Table 302.1. Where “Yes” is selected, the administrative provisions of Chapter 1 of this code and the provisions of ASHRAE 189.1 listed in Chapter 12 shall apply and the remainder of this code shall not apply. Residential buildings not with the scope of ASHRAE 189.1 shall comply with ICC 700 and the jurisdiction shall indicate in Table 302.1 the environmental performance level for such residential buildings.

- The jurisdiction shall indicate the minimum number of project electives that must be incorporated into all projects, as modified by Section 303.2.

- Where “Yes” or “No” boxes are provided, the jurisdiction shall check the box to indicate “Yes” where that section or appendix is to be enforced as a mandatory requirement in the jurisdiction, or “No” where that section or appendix is not to be enforced as a mandatory requirement in the jurisdiction.

  - Where “Yes” is selected for enhanced construction material and waste management in Table 302.1, the jurisdiction shall indicate the minimum percentage of construction waste that is required to be recycled in accordance with Section 502.1 by checking the box in Table 302.1 corresponding to 50% or 65%.

  - Where “Yes” is selected for enhanced plumbing fixture and flow rates in Table 302.1, the jurisdiction shall indicate the minimum flow rates required in accordance with Section 702.1 by checking the box in Table 302.1 corresponding to Tier 1 or Tier 2.

  - Where “Yes” is selected for enhanced energy performance for buildings pursuing performance based compliance and buildings greater than 25,000 square feet in total building floor area, the jurisdiction shall indicate a TANEU of 63 or less in Table 602.1 for each occupancy for which it intends to require enhanced energy performance.

  - Where “Yes” is selected for Appendix B, the jurisdiction shall select a compliance level phase in accordance with Section B103.1 by checking a box in Table 302.1 corresponding to Phase1, 2, 3 or 4. The selection of higher phases requires that all lower phases be selected.

    - Where Phase 1 is selected, the jurisdiction shall indicate the number of months to be used in association with Section B103.2.

    - Where Phase 2 is selected, the jurisdiction shall indicate the number of years and the percentage to be used in association with Section B103.3.

    - Where Phase 3 is selected, the jurisdiction shall indicate the number of years to be used in association with Section B103.4.

    - Where Phase 4 is selected, the jurisdiction shall indicate the number of years and the percentage to be used in association with Section B103.5.

  - Where “Yes” is selected for other jurisdictional requirements in Table 302.1, the provisions of the indicated section shall apply.

302.1.1 TANEU of 63 or less. Where a TANEU of 63 or less is indicated by the jurisdiction in Table 602.1, buildings shall comply on a performance-basis in accordance with Section 602.3.2.

Exception: Buildings less than 25,000 square feet in total building floor area pursuing compliance on a prescriptive basis shall be deemed to have a TANEU of 70 in accordance with Section 602.3.1 and shall not be required to comply with the TANEU of Jurisdictional Choice indicated by the jurisdiction in Table 602.1.

tABLE 302.1

REQUIREMENTS Determined by the jurisdiction

| Section | Section Title or Description and Directives | Jurisdictional Requirements |
| --- | --- | --- |
| CH 1. ADMINISTRATION |
| 102.4.12 302.1 (1) | ICC 700 Environmental Performance Level - Select one box. | ( Bronze ( Silver ( Gold ( Emerald |
| CH 3. JURISDICTIONAL REQUIREMENTS AND PROJECT ELECTIVES |
| 302.1 (2) | Optional compliance path – ASHRAE 189.1 | ( Yes | ( No |
| 302.1 (3) | Project Electives – The jurisdiction shall indicate a number between 0 and 14 to establish the minimum total number of project electives that must be satisfied. | ____ |
| CH 4. SITE DEVELOPMENT AND LAND USE |
| 402.2.1.2 | Floodplain preservation | ( Yes | ( No |
| 402.2.3 | Conservation area | ( Yes | ( No |
| 402.2.5 | Agricultural land | ( Yes | ( No |
| 402.2.6 | Greenfields | ( Yes | ( No |
| 403.4.1 | High occupancy vehicle parking | ( Yes | ( No |
| 403.4.2 | Low emission, hybrid and electric vehicle parking | ( Yes | ( No |
| 405.1 | Light pollution control | ( Yes | ( No |
| CH 5. MATERIAL RESOURCE CONSERVATION AND EFFICIENCY |
| 502.1 | Enhanced construction material and waste management | ( Yes | ( No |
| 502.1 | Minimum percentage of waste material diverted from landfills - Select a percentage only where “Yes” is selected in the previous row. | ( 50% ( 65% |
| CH 6. ENERGY CONSERVATION AND EARTH ATMOSPHERIC QUALITY |
| 602.1, 602.3, 602.3.2, 302.1.1 | Enhanced energy performance - for buildings pursuing performance based compliance and buildings greater than 25,000 square feet in total building floor area | ( Yes | ( No |
| Table 602.1, 302.1, 302.1.1 | TANEU of Jurisdictional Choice - Where “Yes” is selected in the previous row, the jurisdiction shall indicate a TANEU of 63 or less in Table 602.1 for each occupancy for which it intends to require enhanced energy performance. | See Table 602.1 and Section 302.1 |
| 602.3.2.4 | Reduced CO2e emissions calculations and reporting | ( Yes | ( No |
| 613.2 | Post C. of O. TANEU, energy demand, and CO2e emissions reporting | ( Yes | ( No |
| CH 7. WATER RESOURCE CONSERVATION AND EFFICIENCY |
| 702.1.2 | Enhanced plumbing fixture and fitting flow rates | ( Yes | ( No |
| 702.1.2 | Enhanced plumbing fixture and fitting flow rate tier – Select a tier only where “Yes” is selected in the previous row. | ( Tier 1 ( Tier 2 |
| 702.7 | Municipal reclaimed water. | ( Yes | ( No |
| CH 9. COMMISSIONING, OPERATION AND MAINTENANCE |
| 904.1.1.1 | Periodic reporting | ( Yes | ( No |
| CH 10. EXISTING BUILDINGS |
| 1007.2 | Demolition | ( Yes | ( No |
| 1007.3 | Sale of existing buildings and tenant spaces | ( Yes | ( No |
| 1007.4 | Evaluation of existing buildings | ( Yes | ( No |
| APPENDICES |
| Appendix B | Greenhouse gas reduction in existing buildings | ( Yes | ( No |
| B103.1 | Compliance level – The jurisdiction to select phases only where “Yes” is selected in the previous row. | ( Phase 1 ( Phase 2 ( Phase 3 ( Phase 4 |
| B103.2 | Where “Phase 1” is selected under Section B103.1 – jurisdiction to indicate the number of months to be used in association with Section B103.2. | ______ months |
| B103.3 | Where “Phase 2” is selected under Section B103.1 – jurisdiction to indicate the number of years and the percentage to be used in association with Section B103.3. | ______ years ______ % |
| B103.4 | Where “Phase 3” is selected under Section B103.1 – jurisdiction to indicate the number of years to be used in association with Section B103.4. | ______ years |
| B103.5 | Where ” Phase 4” is selected above – jurisdiction to indicate the number of years and the percentage to be used in association with Section B103.5. | ______ years ______ % |
| Appendix C | Sustainability measures | ( Yes | ( No |
| Appendix D | Enforcement procedures | ( Yes | ( No |

SECTION 303

PROJECT electives

303.1 Electives required. A total of not less than the number of project electives indicated in Table 302.1 shall be selected by the owner or registered design professional. Such electives shall be applied as mandatory requirements to the project and shall be indicated to the code official by means of completion of Table 303.1.

303.2 Additional elective. Where required in accordance with Section 705.1, the total number of project electives indicted in Table 302.1 shall be increased by one.

303.3 Applicability to existing buildings. Project electives shall be applicable to existing buildings only where such buildings are evaluated in accordance with Section 1007.4.

303.4 Project electives checklist. The submitted construction documents shall include a completed copy of Table 303.1 indicating which project electives that the owner or registered design professional has selected as a means to comply with Section 303.1. The total number of project electives selected shall be in accordance with the minimum number of project electives indicated by the jurisdiction in Table 302.1.  The Project electives selected shall be applied and enforced as mandatory requirements.

TABLE 303.1

PROJECT ELECTIVES CHECKLIST

| Section | Description | Check the corresponding box to indicate each project elective selected. |
| --- | --- | --- |
| CH 3. JURISDICTIONAL REQUIREMENTS AND PROJECT ELECTIVES |
| 304.1 | Whole Building Life Cycle Assessment | ( |
| CH 4. SITE DEVELOPMENT AND LAND USE |
| 407.2.1 | Flood hazard avoidance | ( |
| 407.2.2 | Agricultural land | ( |
| 407.2.3 | Infill site | ( |
| 407.2.4 | Brownfield site | ( |
| 407.2.5 | Greenfield development | ( |
| 407.2.6 | Greenfield proximity to development | ( |
| 407.2.7 | Greenfield proximity to diverse uses | ( |
| 407.3.1 | Changing and shower facilities | ( |
| 407.3.2 | Long term bicycle parking and storage | ( |
| 407.3.3 | Preferred parking | ( |
| 407.4.1 | Site hardscape 1 | ( |
| 407.4.2 | Site hardscape 2 | ( |
| 407.4.3 | Site hardscape 3 | ( |
| 407.4.4 | Roof covering | ( |
| 407.5 | Light pollution | ( |
| CH 5. MATERIAL RESOURCE CONSERVATION AND EFFICIENCY |
| 507.2 | Waste management (502.1 + 20%) | ( |
| 507.3(1) | Reused, recycled content, recyclable, bio-based and indigenous materials (50%) | ( |
| 507.3(2) | Reused, recycled content, recyclable, bio-based and indigenous materials (80%) | ( (2 Electives) |
| 507.4(1) | Multi-story building – footprint reduced by at least 45% | ( |
| 507.4(2) | Multi-story buildings – footprint reduced by at least 70% | ( (2 Electives) |
| 507.5 | Reduced building volume | ( |
| 507.6.1 | Service life – 100 year design service life category | ( |
| 507.6.1 | Service life – 200 year design service life category | ( (2 Electives) |
| 507.6.2 | Interior adaptability | ( |
| 507.7 | Moisture control | ( |
| CH 6. ENERGY CONSERVATION, EFFICIENCY AND EARTH ATMOSPHERIC QUALITY |
| 613.3.1 | Project TANEU is at least 7 points lower than required by Table 302.1. | ( |
| 613.3.2 | Project TANEU is at least 14 points lower than required by Table 302.1 | ( (2 Electives) |
| 613.3.3 | Project TANEU is at least 21 points lower than required by Table 302.1 | ( (3 Electives) |
| 613.3.4 | Project TANEU is at least 28 points lower than required by Table 302.1 | ( (4 Electives) |
| 613.3.5 | Project TANEU is at least 35 points lower than required by Table 302.1 | ( (5 Electives) |
| 613.3.6 | Project TANEU is at least 42 points lower than required by Table 302.1 | ( (6 Electives) |
| 613.3.7 | Project TANEU is at least 49 points lower than required by Table 302.1 | ( (7 Electives) |
| 613.3.8 | Project TANEU is at least 56 points lower than required by Table 302.1 | ( (8 Electives) |
| 613.3.9 | Project TANEU is at least 63 points lower than required by Table 302.1 | ( (9 Electives) |
| 613.3.10 | Project TANEU is at least 70 points lower than required by Table 302.1 | ( (10 Electives) |
| 613.4 | Building thermal envelope systems | ( |
| 613.5 | Mechanical systems | ( |
| 613.6 | Passive design | ( |
| CH 7. WATER RESOURCE CONSERVATION AND EFFICIENCY |
| 710.2.1 | Fixture flow rates are one tier above that required by Table 302.1 | ( |
| 710.2.1 | Fixture flow rates are two tiers above that required by Table 302.1. | ( (2 Electives) |
| 710.3 | On-site wastewater treatment | ( |
| 710.4 | Non-potable outdoor water supply | ( |
| 710.5 | Non-potable water for plumbing fixture flushing | ( |
| 710.6 | Automatic fire sprinkler system | ( |
| 710.7 | Non-potable water supply to fire pumps | ( |
| 710.8 | Non-potable water for industrial process makeup water | ( |
| 710.9 | Efficient hot water distribution system | ( |
| 710.10 | Non-potable water for cooling tower makeup water | ( |
| 710.11 | Graywater collection | ( |
| CH 8 INDOOR ENVIRONMENTAL QUALITY AND COMFORT |
| 809.2.1 | VOC emissions - flooring | ( |
| 809.2.2 | VOC emissions – ceiling systems | ( |
| 809.2.3 | VOC emissions- wall systems | ( |
| 809.2.4 | Total VOC limit | ( |
| 809.3 | Views to building exterior | ( |

SECTION 304

whole building life cycle assessment

304.1 Whole building life cycle assessment project elective. A whole building life cycle assessment shall be a project elective. The requirements for the execution of a whole building life cycle assessment shall be performed in accordance with the following. Where a whole building life cycle assessment is performed in accordance with Section 304.1, compliance with Section 503 shall not be required. The data and final report shall be included in the owner education manual required by Section 904.4.

- The assessment shall demonstrate that the building project achieves not less than a 20 percent improvement in environmental performance for each of at least three of the following impact measures as compared to a reference building of similar useable floor area, function and configuration that meets the minimum energy requirements of this code and the structural requirements of the International Building Code:

1.1 Primary energy use

1.2 Global warming potential

1.3 Acidification potential

1.4 Eutrophication potential

1.5 Ozone depletion potential

1.6 Smog potential

- The reference and project buildings shall utilize the same life cycle assessment tool.

- Building operational energy shall be included.

- Building process energy shall be permitted to be included.

- The service life of the reference building shall be in accordance with Section 504.1 and shall be not less than 25 years.

- Maintenance and replacement schedules and actions for components shall be included in the assessment.

- The full life cycle, from resource extraction to demolition and disposal, including but not limited to, on-site construction, maintenance and replacement, and material and product embodied acquisition, process and transportation energy, shall be assessed.

- The complete building envelope, structural elements, inclusive of footings and foundations, and interior walls, floors and ceilings, including interior and exterior finishes, shall be assessed to the extent that data is available for the materials being analyzed in the selected life cycle assessment tool.

Chapter 4

Site Development and Land Use

SECTION 401

GENERAL

401.1 Scope and intent. This chapter provides requirements for the development and maintenance of building and building sites that encourage natural resource conservation and environmentally responsible land use and development.

401.2 Other regulations.  Where differences occur between the provisions of this code and the provisions of other locally adopted land use, zoning or site development regulations, the provisions of the most restrictive code or regulation shall apply.

SECTION 402

PRESERVATION OF NATURAL RESOURCES

402.1 General.   In order to limit the use of, and impact on, natural resources, development of a building site shall comply with Sections 402.2 through 402.3.6.

402.2 Protection by Area.  Where park lands, agricultural lands, floodplains, conservation areas, greenfields and surface water bodies or wetlands are located on, or adjacent to, a lot, the development of the lot as a building site shall comply with the provisions of Sections 402.2.1 through 402.2.6.

402.2.1 Floodplains.  For sites located within floodplains, development of buildings and associated site improvements shall comply with either Section 402.2.1.1 or 402.2.1.2.

402.2.1.1 Development in flood hazard areas.  Buildings and structures constructed in a flood hazard area shall be in compliance with Section 1612 of the International Building Code.  The floor elevation of buildinsg or portions of buildings intended for human occupancy shall provide a freeboard of not less than one foot above the design flood elevation as determined by the jurisdiction.

402.2.1.2 Floodplain preservation.  Where this section is indicated to be applicable in Table 302.1, site disturbance or development of land shall not be permitted within a floodplain.

402.2.2 Surface water protection.  Building and building site improvements shall not be located: within 50 feet of a wetland: or within 50 feet of a water body, as defined as the ordinary high-water mark of seas, lakes, rivers, streams and tributaries which support or could support fish, recreation or industrial use.

Exception:  Buildings and associated site improvements specifically related to the use of the water including, but not limited to, piers, docks, fish hatcheries, and habitat restoration facilities, shall be permitted where the impacts of the construction and location adjacent to or over the water on the habitat is mitigated.

402.2.3 Conservation area.  Where this section is indicated to be applicable in Table 302.1, site disturbance or development of land within 50 feet of any designated conservation area shall not be permitted.

402.2.4 Park land. Site disturbance of development of land located within a public park shall not be permitted.

Exceptions:

- Buildings and associated site improvements shall be permitted to be located within a park where the building and associated site improvements serve a park related purpose.

- Park lands owned and managed by the Federal government shall be exempt from this prohibition.

- Privately held property located within the established boundary of a park shall be exempt from this prohibition.

402.2.5 Agricultural land.  Where this section is indicated to be applicable in Table 302.1, buildings and associated site improvements shall not be located on land zoned for agricultural purposes.

Exception: Buildings and associated site improvements shall be permitted to be located on agriculturally zoned land where the building serves an agriculturally related purpose, including, but not limited to, farm produce storage, processing and shipping.

402.2.6 Greenfield sites.   Where this section is indicated to be applicable in Table 302.1, site disturbance or development shall not be permitted on greenfield sites.

Exception:  The development of new buildings and associated site improvements shall be permitted on greenfield sites where the jurisdiction determines that adequate infrastructure exists, or can be provided, and where the sites comply with at least one of the following:

- The greenfield site is located within 1/4 mile of developed residential land with an average density of not less than 8 dwelling units per acre.

- The greenfield site is located within ¼ mile distance, measured over roads or designated walking surfaces, of not less than 5 diverse uses and within ½ mile walking distance of not less than 7 diverse uses.  The diverse uses shall include at least one use from each of the following categories of diverse uses: retail, service, community facility.

- The greenfield site has access to transit service.  The building on the building site shall be located in compliance with one of the following:

3.1. Within ¼ mile distance, measured over roads or designated walking surfaces, of existing or planned bus or streetcar stops.

3.2. Within ½ mile distance, measured over roads or designated walking surfaces, of existing or planned bus, streetcar or rapid transit stops, light or heavy passenger rail stations, ferry terminals, or tram terminals.

- The greenfield site is located adjacent to areas of existing development that have connectivity of not less than 90 intersections per square mile.  Not less than 25 percent of the perimeter of the building site shall adjoin, or be directly across a street, public bikeway or pedestrian pathway from the qualifying area of existing development.

4.1. Intersections included for determination of connectivity shall include the following:

4.1.1.  Intersections of public streets with other public streets,

4.1.2.  Intersections of public streets with bikeways and pedestrian pathways that are not part of a public street for motor vehicles, and

4.1.3.  Intersections of bikeways and pedestrian pathways that are not part of a public street for motor vehicles with other bikeways and pedestrian pathways that are not part of a public street for motor vehicles.

4.2. The following areas need not be included in the determination of connectivity:

4.2.1.  Water bodies, including, but not limited to lakes and wetlands.

4.2.2. Parks larger than 1/2 acre, designated conservation areas and areas preserved from development by the jurisdiction or by the state or federal government.

4.2.3.  Large facilities including, but not limited to airports, railroad yards, college and university campuses.

402.3 Site design and development. The design and development of buildings and associated site improvements shall comply with the site design, water management, vegetation management, soil management and waste management requirements of Sections 402.3.1 through 402.3.6.

402.3.1 Predesign site inventory and assessment. The registered design professional in responsible charge for the project shall submit an inventory and assessment of the natural resources and baseline conditions of the building site to:

- Determine the location of any protection areas identified in Section 402.2 that are located on, or adjacent to the building site;

- Determine whether, and to the degree to which, the native soils and hydrological conditions of the building site have been disturbed and altered by previous use or development; and

3. 	Identify invasive vegetation on the site.

To the extent that the site inventory and assessment affected the design of the proposed development of the building and associated site improvements, it shall be included in the submittal documents for permit application.

402.3.2 Stormwater management. Stormwater management systems, including, but not limited to, infiltration, evapo-transpiration; rainwater harvest and runoff reuse; shall be provided and maintained on the building site.  Stormwater management systems shall address the increase in runoff that would occur resulting from development on the building site and shall either:

- Manage rainfall on-site and size the management system to retain, at a minimum, the volume of a single storm which is equal to the 95th percentile rainfall event and all smaller storms and maintain the predevelopment natural temperature of the runoff; or

2. 	Maintain or restore the pre-development stable, natural runoff hydrology of the site throughout the development or redevelopment process.  Post construction runoff rate, volume, duration, and temperature shall not exceed predevelopment rates.   The stormwater management system design shall be based, in part, on a hydrologic analysis of the building site.

The stormwater management system shall not redirect or concentrate off-site discharge that would harm adjoining lots or public property.

402.3.3  Irrigation systems. Irrigation systems for exterior landscaping shall comply with Sections 402.3.3.1 and 402.3.3.2.

402.3.3.1 Water for outdoor landscape irrigation systems.  Water used in outdoor landscape irrigation systems shall comply with Sections 402.3.3.1.1 through 402.3.3.1.4.

402.3.3.1.1   Potable water. Potable water shall not be used for landscape irrigation purposes.

Exceptions:  Potable water is permitted to be used in irrigation systems as follows:

- During the establishment phase of newly planted landscaping. The establishment phase shall be not longer than the following:

                - 1.1. 3 years for trees

  - 1.2. 2 years for shrubs

  - 1.3. 1 year for herbaceous cover plants

- To irrigate food production.

- To supplement non-potable water irrigation of shade trees provided in accordance with

- Potable water is permitted for landscape irrigation when approved by local ordinance or regulation.

402.3.3.1.2 Graywater systems. Graywater systems used for landscape irrigation purposes shall be limited to subsurface and surface irrigation applications only. Retention time for surface irrigation 24 hours or less.  Graywater to be used in graywater irrigation shall comply with the provisions of Section 708 other than Sections 708.6 and 708.12.6.5. Subsurface graywater systems shall be in accordance with Section 406.2. Graywater shall be filtered by a 100 micron or finer filter.   The control panel for the graywater irrigation system shall be provided with signage in accordance with Section 706.2.

402.3.3.1.3 Municipal reclaimed water. Municipal reclaimed water used for landscape irrigation purposes shall be limited to subsurface applications.  Reclaimed water used in irrigation systems shall comply with the provisions of Section 709 except for Section 709.5.  Reclaimed water shall be filtered by a 100 micron or finer filter.   The control panel for the reclaimed water irrigation system shall be provided with signage in accordance with Section 706.2

Exception:  Subject to the approval of the code official based on the extent of purification occurring in reclamation process, municipal reclaimed water shall be permitted in sprinkler irrigation applications.

402.3.3.1.4 Collected rainwater.  Rainwater collected on the surface of the building site, or from the roof surfaces of the building, and used for landscape irrigation purposes shall not be limited regarding the method of application.  Rainwater collected from elevated building locations that is to be used in building site irrigation, shall be in compliance with the provisions of Section 707 other than Sections 707.6, 707.12.1, 707.12.1.1 and 707.12.7.4.

402.3.3.2 Irrigation system design and installation. Landscape irrigation systems shall be designed and installed to provide the minimum amount of irrigation required for maintenance of vegetation in the landscaping of the building site.   The systems shall utilize drip irrigation, soaker hoses, subsurface and surface irrigation, where practicable.  Landscape irrigation systems shall not direct spray onto building exterior surfaces or exterior paved surfaces.

402.3.4 Outdoor ornamental fountains and water features.   Outdoor ornamental fountains and other water features constructed or installed on a building site shall be supplied with either municipally reclaimed or collected rainwater complying with Section 402.3.3.1. Signage in accordance with Section 706.2, shall be posted at each outdoor fountain and water feature where non-potable water is used.

402.3.5 Management of vegetation, soils and erosion control.  During construction on a building site, vegetation and soils shall be protected and reused as provided in Sections 402.3.5.1 through 402.3.5.7.

402.3.5.1 Landscape, soil and water quality protection plan.  A soil and water quality protection plan shall be submitted by the registered design professional and approved prior to construction. The protection plan shall be in accordance with Section 406.5.

402.3.5.2 Vegetation and soil protection.  Where existing soils and vegetation are to be protected, a vegetation and soil protection plan establishing designated vegetation and soil protection areas (VSPA’s) shall be submitted with the construction drawings and other submittal documents.  The protection plan shall be in accordance with Section 406.3.

402.3.5.3 Topsoil protection.  Topsoil that could potentially be damaged by construction activities or equipment shall be removed from areas to be disturbed and stockpiled on the building site for future reuse on the building site or other approved location. Topsoil stockpiles shall be secured and protected throughout the project with temporary or permanent soil stabilization measures to prevent erosion or compaction.

402.3.5.4 Soil reuse and restoration.  Soils that are being placed or replaced on a building site shall be prepared, amended and placed in a manner that establishes or restores the ability of the soil to support the vegetation that has been protected and that will be planted.  Soil reuse and restoration shall be in accordance with Section 406.4.

402.3.5.5 Imported soils.  Topsoils or soil blends imported to a building site to serve as topsoil shall not be mined from the following locations:

- Sites that are prime farmland, unique farmland, or farmland of statewide importance.

- Greenfield sites where development is prohibited by Section 402.2.6.

Exception:  Soils shall be permitted to be imported from the locations in Items 1 and 2 where those soils are a byproduct of a building and building site development process provided that imported soils are reused for functions comparable to their original function.

402.3.5.6 Invasive species.  Invasive species shall not be planted on a building site.  Any invasive plants currently on the site shall be removed.  Existing vegetation that is to be retained on a building site shall be protected as required by Section 402.3.5.2.

402.3.5.7 Documentation.  Documentation demonstrating compliance with Section 402.3.5 shall be provided as part of the submittal documents and during the construction and inspection process.

402.3.6 Building site waste management plan.   A building site waste management plan shall be developed and implemented to recycle or salvage not less than 75 percent of the land-clearing debris and excavated soils.  Land-clearing debris includes rock, trees, stumps and associated vegetation.  The plan shall include provisions that address all of the following:

- Materials to be diverted from disposal by efficient usage, recycling or reuse on the building site shall be specified.

- Diverted materials shall not be sent to sites that are agricultural land, floodplain areas or greenfield sites where development is prohibited by Section 402.2.

- The removal and disposal off-site of invasive plant species.

- Where contaminated soils are removed, the methods of removal and location where the soils are to be treated and disposed.

- The amount of materials to be diverted shall be specified and shall be calculated by weight or volume, but not both.

Construction materials and waste and hardscape materials removed during site preparation shall be managed in accordance with Section 502.1.

SECTION 403

Transportation impact

403.1 Walkways and bicycle paths.  Independent, paved walkways and bicycle paths suitable for bicycles, strollers, pedestrians, and other forms of non-motorized locomotion shall be provided where vehicular access roads are constructed on a building site.  Walkways and bicycle paths shall connect to existing paths or sidewalks, and shall be designed to connect to any planned future paths.

403.2 Changing and shower facilities. Buildings with an total building floor area greater than 10,000 square feet and that are required to be provided with long term bicycle parking and storage in accordance with Section 403.3 shall be provided with on-site changing room and shower facilities.  Not less than one shower shall be provided for each 200 employees, or fraction thereof.

Exceptions:

- Where only one changing room and shower facility is required, the changing room and shower facility shall be permitted to be a single facility available to all occupants.

- Changing and shower facilities need not be provided within a Group E occupancy serving students in the 6th grade or younger.

403.3 Bicycle parking and storage.  Long term and short term bicycle parking shall be provided as specified in Table 403.3.  Bicycle parking is not required for uses and occupancies not listed in Table 403.3.   The required minimum number of spaces shall be determined based upon the occupied floor area of each primary use or occupancy of building.  Accessory occupancy areas shall be included in the calculation of primary occupancy area.

Exceptions:

- Long term bicycle parking shall not be required where the total building floor area is less than 2,500 square feet.

- Subject to the approval of the code official, the number of bicycle parking spaces shall be permitted to be reduced due to building site characteristics including, but not limited to, isolation from other development.

403.3.1 Short term bicycle parking.  Short term bicycle parking shall comply with all of the following:

1.  Shall be located outside of buildings at locations within 100 feet of and visible from the main entrances;

2.  Shall be provided with illumination of not less than 1 footcandle at the parking surface;

3.  Shall be located at the same grade as the sidewalk or at a location reachable by ramp or accessible route;

4.  Shall have an area of not less than 18 inches by 60 inches per bicycle;

5.  Shall be provided with a rack or other facility for locking or securing each bicycle.

Exception:  Where directional signage is provided at the main building entrances, short term bicycle parking shall be permitted to be located inside a building or at locations not visible from the main entrance.

403.3.2 Long term bicycle parking.  Long term bicycle parking shall comply with all of the following:

1.  Shall be located on the same site and within the building or within 300 feet of the main entrances;

2.  Shall be provided with illumination of not less than 1 footcandle at the parking surface;

3.  Shall have an area of not less than 18 inches by 60 inches feet per bicycle; and

4.  Shall be provided with a rack or other facility for locking or securing each bicycle.

Not less than 50 percent of long term bicycle parking shall be within a building or provided with a permanent cover including, but not limited to, roof overhangs, awnings, or bicycle storage lockers.

Vehicle parking spaces, other than those required by Section 403.4 and accessible parking required by the International Building Code, shall be permitted to be used for the installation of long term bicycle parking spaces.

403.4 Vehicle parking.  Where either Section 403.4.1 or 403.4.2 is indicated to be applicable in Table 302.1, parking provided at a building site shall comply with this section.  Parking spaces required by this section shall be those in the parking facility that are located on the shortest route of travel from the parking facility to a building entrance, but shall not take precedence over parking spaces that are required to be accessible in accordance with the International Building Code.  Where buildings have multiple entrances with adjacent parking, parking spaces required by this section shall be dispersed and located near the entrances.  Such parking spaces shall be provided with approved signage that specifies the permitted usage.

403.4.1 High occupancy vehicle parking.  Where employee parking is provided for a building that has an total building floor area greater than 10,000 square feet and that has a building occupant load greater than 100, at least 5 percent, but not less than 2, of the parking spaces provided shall be designated as preferred parking for high occupancy vehicles.

403.4.2 Low emission, hybrid, and electric vehicle parking. Where parking is provided for a building that has an total building floor area greater than 10,000 square feet and that has an building occupant load greater than 100, at least 5 percent, but not less than 2, of the parking spaces provided shall be designated as preferred parking for low emission, hybrid, and electric vehicles.

TABLE 403.3

BICYCLE PARKINGa

| Occupancy | Specific Use | Short term spaces | Long Term spacesb, c |
| --- | --- | --- | --- |
| R-1 | Hotel, motel, boarding houses | None | 1 per 50 employees; not less than 2 spaces |
| R-2, R-3, R-4 | All | None | None |
| A-1 | Movie theaters | 1 per 50 seats; not less than 4 spaces | 1 per 50 employees; not less than 2 spaces |
|  | Concert hall, Theaters other than for movies | 1 per 500 seats |  |
| A-2 | Restaurants | 1 per 50 seats; not less than 2 spaces |  |
| A-3 | Places of worship | 1 per 500 seats |  |
|  | Assembly spaces other than places of worship | 1 per 25,000 square feet; not less than 2 spaces |  |
| A-4 – A-5 | All | 1 per 500 seats |  |
| B | All | 1 per 50,000 square feet; not less than 2 spaces | 1 per 25,000 square feet; not less than 2 spaces |
| F, H, S | All, except parking facilities | None | 1 per 50 employees; not less than 2 spaces |
| M | All | 1 per 25,000 square feet; not less than 2 spaces | 1 per 50,000 square feet; not less than 2 spaces |
| S | Transit park and ride lots | None | 1 per 20 vehicle parking spaces. |
|  | Commercial Parking facility | 1 per 20 vehicle parking spaces | None |
| I-2 | All | 1 per 25,000 square feet; not less than 2 spaces | 1 per 50 employees; not less than 2 spaces |
| I-1 | All | None |  |
| E, I-4 | Day Care | None |  |
| E | Schools | None | 1 per 10 students |
| Other | Outdoor recreation, parks | 1 per 20 vehicle parking spaces; not less than 2 spaces | None |

- Requirements based on square feet shall be the occupied floor area of the occupancy or use.

- Employees shall be based on the number of full time equivalent employees during the largest shift.

- When a calculations results in a fraction of a space, the requirement shall be rounded to the next higher whole number.

SECTION 404

HEAT ISLAND MITIGATION

404.1 General.  The heat island effect of building and building site development shall be mitigated in accordance with Sections 404.2 and 404.3.

404.2 Site Hardscape. In climate zones 1 through 6, as established in the International Energy Conservation Code, not less than 50 percent of the site hardscape shall be provided with one or any combination of options described in Sections 404.2.1 through 404.2.4. For the purposes of this section, site hardscape shall not include areas of the site covered by solar photovoltaic arrays or solar thermal collectors.

404.2.1 Site hardscape materials. Hardscape materials shall have a minimum initial Solar Reflectance Index of 29 when determined in accordance with ASTM E1980 using a convection coefficient of 2.1 Btu/h-ft2 (12 W/m2*k).

404.2.2 Shading structures. Where shading is provided by a structural device or element, such device or element shall comply with all of the following:

1.	Where open trellis-type free standing structures such as, but not limited to, covered walkways, and trellises or pergolas, are covered with native plantings, they shall be designed to achieve mature coverage within five years;

2.	Parking shading structures shall comply with Section 404.3;

3.	Shade provided onto the hardscape by an adjacent building or structure located on the same lot shall be calculated and credited toward compliance with this section based on the projected peak sun angle on the summer solstice.

404.2.3 Shade by trees. Where shading is provided by trees, such trees shall be selected and placed in accordance with all of the following:

1.	Trees selected shall be those that are native to the region and climate zone in which the project site is located. Plantings shall be selected and sited to produce a hardy and drought resistant vegetated area;

2.	Construction documents shall be submitted that show the planting location and anticipated five year canopy growth of all trees and that show the contributions of existing tree canopies; and

3.	Shading calculations shall be shown on the construction documents demonstrating compliance with this section and shall include only those hardscape areas directly beneath the trees based on a five year growth canopy. Duplicate shading credit shall not be granted for those areas where multiple trees shade the same hardscape.

404.2.4 Open-grid pavers and open-graded aggregate. Open-grid pavers and open-graded aggregate shall be permitted where the use of these types of hardscapes do not interfere with fire and emergency apparatus or vehicle or personnel access and egress, utilities, or telecommunications lines. Aggregate used shall be of uniform size.

404.3 Roof coverings.  Not less than 75 percent of the roof surfaces of buildings located in climate zones 1 through 3, as established in the International Energy Conservation Code, shall be in compliance with Section 404.3.1 or 404.3.2, or a combination of both methods.

Exception:  Portions of roof surfaces where solar thermal collectors and solar photovoltaic systems are provided shall be permitted to be deducted from the roof surface required to comply with this section.

404.3.1 Roof solar reflectance and thermal emittance. Where roof coverings are used for compliance with Section 404.3, roof coverings shall comply with Section 404.3.1.1 or 404.3.1.2. The values for solar reflectance and thermal emittance shall be determined by an independent laboratory accredited by a nationally recognized accreditation program. Roof products shall be labeled and certified by the manufacturer demonstrating compliance.

404.3.1.1 Roof products testing. Roof products shall be tested for a minimum three-year aged solar reflectance and thermal emittance in accordance with CRRC-1, and shall comply with the minimum values in Table 404.3.1.

404.3.1.2 Solar reflectance index. Roof products shall be permitted to use a Solar Reflectance Index (SRI) where the calculated value is in compliance with Table 404.3.1 values for Minimum Aged SRI. The SRI value shall be determined using ASTM E1980 with a convection coefficient of 2.1 Btu/h-ft2 (12 W/m2*k) based on three-year aged roof samples tested in accordance with CRRC-1.

TABLE 404.3.1

REFLECTANCE AND EMITTANCE

| Roof Slope | Minimum Aged Solar Reflectance | Minimum Aged Thermal Emittance | Minimum Aged SRI |
| --- | --- | --- | --- |
| Less than 2:12 | 0.55 | 0.75 | 60 |
| 2:12 or greater | 0.30 | 0.75 | 25 |

404.3.2 Vegetative roofs.  Roofs shall be covered with either an extensive or intensive vegetative roof.  Vegetative roofs shall comply with Section 406.6.

SECTION 405

SITE LIGHTING

405.1 Light pollution control.  Where this section is indicated to be applicable in Table 302.1, uplight, light trespass, and glare shall be limited for all exterior lighting equipment as described in Sections 405.2 and 405.3.

Exceptions: Lighting used for the following exterior applications is exempt where equipped with a control device independent of the control of the non-exempt lighting:

- Specialized signal, directional, and marker lighting associated with transportation;

- Advertising signage or directional signage;

- Lighting integral to equipment or instrumentation and installed by its manufacturer;

- Theatrical purposes, including performance, stage, film production, and video production;

- Athletic playing areas where lighting is equipped with hoods or louvers for glare control;

- Temporary lighting;

- Lighting for industrial production, material handling, transportation sites, and associated storage areas where lighting is equipped with hoods or louvers for glare control;

- Theme elements in theme and amusement parks

- Roadway lighting required by governmental authorities;

- Lighting used to highlight features of public monuments and registered landmark structures.

[E] 405.1.1 Exterior lighting zones.  The lighting zone for the building site is determined from Table 405.1.1 unless otherwise specified by the jurisdiction.

[E] TABLE 405.1.1

EXTERIOR LIGHTING ZONES

| LIGHTING ZONE | DESCRIPTION |
| --- | --- |
| 1 | Developed areas of national parks, state parks, forest land and rural areas |
| 2 | Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas |
| 3 | All other areas |
| 4 | High-activity commercial districts in major metropolitan areas as designated by the local land use planning agency |

405.2 Uplight. All exterior lighting shall comply with the requirements of Table 405.2 for the exterior lighting zones (LZ) appropriate to the building site.

Exception:  Lighting used for the following exterior applications shall be exempt from the requirements of Table 405.2.

1.	Lighting for building facades, landscape features, and public monuments in exterior lighting zones 3 and 4.

2.	Lighting for building facades in exterior lighting zone 2.

TABLE 405.2 
UPLIGHT RATINGS a,b

|  | LZ 1 | LZ 2 | LZ 3 | LZ 4 |
| --- | --- | --- | --- | --- |
| Maximum Luminaire Uplight Rating | U1 | U2 | U3 | U4 |

a.   Uplight ratings are defined by IESNA TM-15-07 Addendum A.

b.  The rating shall be determined by the actual photometric geometry in the specified mounting orientation.

405.3 Light trespass and glare.  Where luminaires are mounted on buildings at locations that are within a distance to the lighting boundary, measured horizontally, that is equal to twice the height that the luminare is mounted, such luminaires shall not exceed the applicable glare ratings specified in Table 406.3(1).   All other exterior luminaries shall not exceed the applicable backlight and glare ratings specified in Table 406.3(2).

Table 405.3(1)
Maximum Glare Ratings for Building Mounted Luminaires Located

Two Mounting Heights or Less from Lighting Boundary a, b, c

|  | LZ1 | LZ2 | LZ3 | LZ4 |
| --- | --- | --- | --- | --- |
| Maximum luminaire glare rating | G0 | G1 | G1 | G2 |

a.  Mounting height is the distance above finished grade at which a luminaire is mounted, measured to the midpoint of the luminaire.

b.  Uplight and glare ratings are defined by IESNA TM-15-07 Addendum A.

c. The rating shall be determined by the actual photometric geometry in the specified mounting orientation.

Table 405.3(2)

Maximum allowable Backlight and Glare Ratings a,b,c

|  | LZ 1 | LZ 2 | LZ 3 | LZ 4 |
| --- | --- | --- | --- | --- |
| Luminaire located more than two mounting heights from lighting boundary | B4 G1 | B4 G2 | B4 G3 | B4 G4 |
| Luminaire located one to two mounting heights from lighting boundary | B3 G1 | B3 G2 | B3 G3 | B4 G4 |
| Luminaire located one-half to one mounting heights from lighting boundary | B2 G1 | B2 G2 | B2 G3 | B3 G4 |
| Luminaire located less than one-half mounting height from lighting boundary | B0 G1 | B0 G2 | B1 G3 | B2 G4 |

a. Backlight and glare ratings are defined by IESNA TM-15-07 Addendum A.

b.  Luminaries located two mounting heights or less from the lighting boundary shall be installed with backlight towards the nearest lighting boundary, unless they are lighting a roadway, bikeway, or walkway that intersects a public roadway.

c.  The rating shall be determined by the actual photometric geometry in the specified mounting orientation.

SECTION 406

Detailed site development requirements

406.1 General. The provisions of this section shall govern the design and installation of site development systems and use of materials.

406.2 Subsurface graywater irrigation systems.  Gravity subsurface gray water irrigation systems, where provided in accordance with Section 402.3.2.2.1, shall be designed and installed in accordance with Sections 406.2.1 through 406.2.6.   Graywater collection and storage systems shall comply with this section and the provisions of Section 708 other than Sections 708.6 and 708.12.6.5.

406.2.1 Estimating graywater discharge. The irrigation system shall be sized in accordance with the gallons-per-day-per-occupant number based on the type of fixtures connected to the graywater system. The discharge shall be calculated by the following equation:

C = (A x B)-D     									(Equation 4-1)

Where:

A = Number of occupants:

Residential—Number of occupants shall be determined by the actual number of occupants, but not less than two occupants for one bedroom and one occupant for each additional bedroom.

Commercial—Number of occupants shall be determined by the International Building Code

B = Estimated flow demands for each occupant:

Residential—25 gallons per day (94.6 Lpd) per occupant for showers, bathtubs and lavatories and 15 gallons per day (56.7 Lpd) per occupant for clothes washers or laundry trays.

Commercial—Based on type of fixture or water use records minus the discharge of fixtures other than those discharging gray water.

C = Estimated gallons graywater discharge based on the total number of occupants.

D= Estimated gallons of graywater to be used within the interior of the building.

406.2.2 Percolation tests. The permeability of the soil in the proposed absorption system shall be determined by percolation tests or permeability evaluation.

406.2.2.1 Percolation tests and procedures. At least three percolation tests in each system area shall be conducted. The holes shall be spaced uniformly in relation to the bottom depth of the proposed absorption system. More percolation tests shall be made where necessary, depending on system design.

406.2.2.1.1 Percolation test hole. The test hole shall be dug or bored. The test hole shall have vertical sides and a horizontal dimension of 4 inches to 8 inches (102 mm to 203 mm). The bottom and sides of the hole shall be scratched with a sharp-pointed instrument to expose the natural soil. All loose material shall be removed from the hole and the bottom shall be covered with 2 inches (51 mm) of gravel or coarse sand.

406.2.2.1.2 Test procedure, sandy soils. The hole shall be filled with clearwater to a minimum of 12 inches (305 mm) above the bottom of the hole for tests in sandy soils. The time for this amount of water to seep away shall be determined, and this procedure shall be repeated if the water from the second filling of the hole seeps away in 10 minutes or less. The test shall proceed as follows:

- Water shall be added to a point not more than 6 inches (152 mm) above the gravel or coarse sand.

- Thereupon, from a fixed reference point, water levels shall be measured at 10-minute intervals for a period of 1 hour.

- Where 6 inches (152 mm) of water seeps away in less than 10 minutes, a shorter interval between measurements shall be used, but in no case shall the water depth exceed 6 inches (152 mm). Where 6 inches (152 mm) of water seeps away in less than 2 minutes, the test shall be stopped and a rate of less than 3 minutes per inch (7.2 s/mm) shall be reported.

- The final water level drop shall be used to calculate the percolation rate.

Soils not meeting the above requirements shall be tested in accordance with Section 406.2.2.1.3.

406.2.2.1.3 Test procedure, other soils. The hole shall be filled with clear water, and a minimum water depth of 12 inches (305 mm) shall be maintained above the bottom of the hole for a 4-hour period by refilling whenever necessary or by use of an automatic siphon. Water remaining in the hole after 4 hours shall not be removed. Thereafter, the soil shall be allowed to swell not less than 16 hours or more than 30 hours. Immediately after the soil swelling period, the measurements for determining the percolation rate shall be made as follows:

- Any soil sloughed into the hole shall be removed and the water level shall be adjusted to 6 inches (152 mm) above the gravel or coarse sand.

- Thereupon, from a fixed reference point, the water level shall be measured at 30-minute intervals for a period of 4 hours, unless two successive water level drops do not vary by more than 1/16 inch (1.59 mm). At least three water level drops shall be observed and recorded.

- The hole shall be filled with clear water to a point not more than 6 inches (152 mm) above the gravel or coarse sand whenever it becomes nearly empty. Adjustments of the water level shall not be made during the three measurement periods except to the limits of the last measured water level drop.

- When the first 6 inches (152 mm) of water seeps away in less than 30 minutes, the time interval between measurements shall be 10 minutes and the test run for 1 hour. The water depth shall not exceed 5 inches (127 mm) at any time during the measurement period.

- The drop that occurs during the final measurement period shall be used in calculating the percolation rate.

406.2.2.1.4  Mechanical test equipment. Mechanical percolation test equipment shall be of an approved type.

406.2.3  Permeability evaluation. Soil shall be evaluated for estimated percolation based on soil structure and texture in accordance with accepted soil evaluation practices. Borings shall be made in accordance with Section 406.2.2.1 for evaluating the soil.

406.2.4 Subsurface landscape irrigation site location. The surface grade of all soil absorption systems shall be located at a point lower than the surface grade of any water well or reservoir on the same or adjoining lots. Where this is not possible, the irrigation system shall be located so that surface water drainage from the building site is not directed toward a well or reservoir. The soil absorption system shall be located with a minimum horizontal distance between various elements as indicated in Table 406.2.4 and as provided in Section 708.14.7.  Surface water shall be diverted away from any soil absorption site on the same or adjoining lots.

TABLE 406.2.4

LOCATION OF GRAYWATER SYSTEM

| ELEMENT | MINIMUM HORIZONTAL DISTANCE (feet) |
| --- | --- |
|  | IRRIGATION DISPOSAL FIELD |
| Buildings | 2 |
| Lot lines other than lot lines adjoining public ways | 5 |
| Water wells | 100 |
| Streams, lakes and wetlands | 50 |
| Seepage pits | 5 |
| Septic tanks | 5 |
| Water service | 5 |
| Public water main | 10 |

406.2.5 Installation. Absorption systems shall be installed in accordance with Sections 406.2.5.1 through 406.2.5.5 to provide landscape irrigation without surfacing of graywater.

406.2.5.1 Absorption area. The total absorption area required shall be computed from the estimated daily graywater discharge and the design-loading rate based on the percolation rate for the site. The required absorption area equals the estimated graywater discharge divided by the design-loading rate from Table 406.2.5.1.

TABLE 406.2.5.1

DESIGN LOADING RATE

| PERCOLATION RATE (minutes per inch) | DESIGN LOADING FACTOR (gallons per square foot per day |
| --- | --- |
| Less than 10 | 1.2 |
| 10 to less than 30 | 0.8 |
| 30 to less than 45 | 0.72 |
| 45 and greater | 0.4 |

For SI: 1 minute per inch = min/25.4 mm,

1 gallon per square foot = 40.7 L/m2.

406.2.5.2 Seepage trench excavations. Seepage trench excavations shall be a minimum of 1 foot (304 mm) to a maximum of 5 feet (1524 mm) wide. Trench excavations shall be spaced a minimum of 2 feet (610 mm) apart. The soil absorption area of a seepage trench shall be computed by using the bottom of the trench area (width) multiplied by the length of pipe. Individual seepage trenches shall be a maximum of 100 feet (30 480 mm) in developed length.

406.2.5.3 Seepage bed excavations. Seepage bed excavations shall be a minimum of 5 feet (1524 mm) wide and have more than one distribution pipe. The absorption area of a seepage bed shall be computed by using the bottom of the trench area. Distribution piping in a seepage bed shall be uniformly spaced a maximum of 5 feet (1524 mm) and a minimum of 3 feet (914 mm) apart, and a maximum of 3 feet (914 mm) and a minimum of 1 foot (305 mm) from the sidewall or headwall.

406.2.5.4 Excavation and construction. The bottom of a trench or bed excavation shall be level. Seepage trenches or beds shall not be excavated where the soil is so wet that such material rolled between the hands forms a soil wire. All smeared or compacted soil surfaces in the sidewalls or bottom of seepage trench or bed excavations shall be scarified to the depth of smearing or compaction and the loose material removed. Where rain falls on an open excavation, the soil shall be left until sufficiently dry so a soil wire will not form when soil from the excavation bottom is rolled between the hands. The bottom area shall then be scarified and loose material removed.

406.2.5.5 Aggregate and backfill. A minimum of 6 inches of aggregate ranging in size from 1/2 to 2-1/2 inches (12.7 mm to 64 mm) shall be laid into the trench below the distribution piping elevation. The aggregate shall be evenly distributed a minimum of 2 inches (51 mm) over the top of the distribution pipe. The aggregate shall be covered with approved synthetic materials or 9 inches (229 mm) of uncompacted marsh hay or straw. Building paper shall not be used to cover the aggregate. A minimum of 9 inches (229 mm) of soil backfill shall be provided above the covering.

406.2.6 Distribution piping. Distribution piping shall be not less than 3 inches (76 mm) in diameter. Materials shall comply with Table 406.2.6.  The top of the distribution pipe shall be not less than 8 inches (203 mm) below the original surface. The slope of the distribution pipes shall be a minimum of 2 inches (51 mm) and a maximum of 4 inches (102 mm) per 100 feet (30 480 mm).

TABLE 406.2.6

DISTRIBUTION PIPE

| Material | Standard |
| --- | --- |
| Polyetheline (PE) plastic pipe | ASTM F405 |
| Polyvinyl chloride (PVC) plastic pipe | ASTM D2729 |
| Polyvinyl chloride (PVC) plastic pipe with pipe stiffness of PS 35 and PS 50 | ASTM F1488 |

406.3 Vegetation and soil protection.  Vegetation and soil protection plans, where provided in accordance with Section 402.3.5, shall address the following:

1. 	Identification of existing vegetation located on a building site that is to be preserved and protected;

2.	Identification of portions of the building site to be designated vegetation and soil protection areas (VSPAs) that are to be protected during the construction process from being affected by construction activities;

3.	Specification of methods to be used such as temporary fencing or other physical barriers to maintain the protection of the designated vegetation and soil protection areas (VSPAs).

4.	Specification of protected perimeters around trees and shrubs that are to be included in the designated vegetation and soil protection areas (VSPAs).  Perimeters around trees shall be not less than 2 feet for every inch of tree diameter and around shrubs shall be not less than twice the radius of the shrub.

Exception:  Approved alternative perimeters appropriate to the location and the species of the trees and shrubs shall be permitted.

5. 	Specification of methods to protect the viability of the designated vegetation and soil protection areas (VSPAs) to support the remaining vegetation at the conclusion of the construction process including minimizing impacts on the existing stormwater drainage patterns associated with the VSPAs.

406.4 Soil reuse and restoration.  Soils that are reused and restored on a building site shall comply with Sections 406.4.1 through 406.4.4.

406.4.1 Preparation.   Before placing stockpiled or imported topsoils, compliance with all of the following shall occur:

1. 	Areas shall be cleared of debris including, but not limited to, building materials, plaster, paints, road base type materials, petroleum based chemicals, and other harmful materials;

2. 	Areas of construction-compacted subsoil shall be scarifiedl; and

3.   The first lift of replaced soil shall be mixed into this scarification zone to improve the transition between the subsoil and overlying soil horizons.

Exception:  Scarification is prohibited in all of the following locations:

1. 	Where scarification would damage existing tree roots.

2. 	On inaccessible slopes.

3. 	On or adjacent to trenching and drainage installations.

4. 	On areas intended by the design to be compacted such as abutments, footings, inslopes.

5. 	Brownfields.

6. 	Other locations where subsoiling would damage existing structures, utilities and vegetation being preserved.

406.4.2 Restoration.  Soils disturbed during construction shall be restored in all areas that will not be covered by buildings, structures or hardscapes.  Soil restoration shall comply with Sections 406.4.2.1 and 406.4.2.2.

      - Organic matter.  To provide appropriate organic matter for plant growth and for water storage and infiltration, soils shall be amended with a mature, stable compost material so that not less than the top 12 inches of soil contains not less than 3 percent organic matter. Sphagnum peat or organic amendments that contain sphagnum peat shall not be used. Soil organic matter shall be determined in accordance with ASTM D2974 or USCC/TMECC 05.07A. Organic materials selected for on-site amendment or for blending of imported soils shall be renewable within a 50-year cycle.

Exception:  Where the reference soil for a building site has an organic level depth other than 12 inches, soils shall be amended to organic matter levels and organic matter depth that are comparable to the site’s reference soil.

406.4.2.2 Additional soil restoration criteria.  In addition to compliance with Section 406.4.2.1, soil restoration shall comply with not less than three of the following criteria:

1.	Compaction.  Bulk densities within the root zone shall not exceed the densities specified in Table 406.4.2.2.  The root zone shall be not less than 12 inches nor less than the site's reference soil, whichever results in the greater depth of measurement.

2.	Infiltration rates.  Infiltration rates or saturated hydraulic conductivity of the restored soils shall be comparable to the site’s reference soil.  Infiltration rates shall be determined in accordance with ASTM D3385 or ASTM D5093. For sloped areas where the methods provided in the referenced standards cannot be used successfully, alternate methods approved by the code official shall be permitted provided that the same method is used to test both reference soil and on-site soil.

3.	Soil biological function.  Where remediated soils are used, the biological function of the soils’ mineralizable nitrogen shall be permitted as a proxy assessment of biological activity.

4.	Soil chemical characteristics.  Soil chemical characteristics appropriate for plant growth shall be restored. The pH, cation exchange capacity and nutrient profiles of the original undisturbed soil or the site’s reference soil shall be matched in restored soils. Salinity suitable for regionally appropriate vegetation shall be established. Soil amendments and fertilizers shall be selected from those which minimize nutrient loading to waterways or groundwater.

TABLE 406.4.2.2

MAXIMUM CONE PENETROMETER READINGS

| Surface Resistance (PSI) | Subsurface Resistance (PSI) |
| --- | --- |
| All Textures Sand | Sand (includes loamy sand, sandy loam, sandy clay loam, and sandy clay) | Silt (includes loam, silt loam, silty clay loam, and silty clay) | Clay (includes clay loam) |
| 110 | 260 | 260 | 225 |

406.4.3 Engineered growing media.  Where engineered growing media are used on-site, including, but not limited to vegetative roofs, trees located within hardscape areas, and special soils specified for wetlands and environmental restoration sites, such media shall comply with the best available science and practice standards for that engineered growing media and use.

406.4.4 Documentation.  The registered design professional shall provide the following to document compliance:

- Documentation, such as receipts from a soil, compost and amendments supplier, to demonstrate that techniques to restore soil occurred;

- Soil test results to demonstrate that the selected techniques achieved the criteria of Sections 406.4.2.1 and 406.4.2.2.  Not less than two soil tests shall be conducted on the building site.  For building sites where more than 8,000 square feet of soil is to be disturbed during construction, there shall be not less than one report for every 4,000 square feet disturbed.

406.5 Landscape, soil and water quality protection plan.  A landscape, soil and water quality protection plan, where provided in accordance with Section 402.3.5.1, shall address the following:

1.	A soils map, site plan, or grading plan that indicates designated soil management areas for all site soils, including, but not limited to:

1.1.	Soils that will be retained in place and designated as vegetation and soil protection areas (VSPAs).

1.2.	Topsoils that will be stockpiled for future reuse and the locations for the stockpiles.

1.3.	Soils that will be disturbed during construction.

1.4.	Soils that will be restored and re-vegetated.

1.5	Soils disturbed by previous development that will be restored in place and re-vegetated.

1.6.	Locations for all laydown and storage areas, parking areas, haul roads and construction vehicle access, temporary utilities and construction trailer locations.

1.7.	Treatment details for each zone of soil that will be restored, including the type, source and expected volume of materials, including compost amendments, mulch and topsoil.

1.8.	A narrative of all measures to be taken to ensure that areas not to be disturbed and areas of restored soils are protected from compaction by vehicle traffic or storage, erosion, and contamination until project completion.

- A written erosion, sedimentation and pollutant control program for construction activities associated with the project. The program shall describe the best management practices (BMPs) to be employed including how the BMPs accomplish the following objectives:

2.1	Prevent loss of soil during construction due to stormwater runoff or wind erosion, including the protection of topsoil by stockpiling for reuse.

2.2.	Prevent sedimentation of stormwater conveyances or receiving waters or other public infrastructure.

2.3.	Prevent polluting the air with dust and particulate matter.

2.4.	Prevent runoff and infiltration of other pollutants from construction site, including, but not limited to thermal pollution, concrete wash, fuels, solvents, hazardous chemical runoff, pH and pavement sealants. Ensure proper disposal of pollutants.

2.5. 	Protect all designated vegetation and soil protection areas, floodplains and other areas of vegetation that will remain on site from construction activities.

- A written periodic maintenance protocol for all landscaping and stormwater management systems, including, but not limited to:

  - A schedule for periodic watering of new planting which reflects different water needs during the establishment phase of new plantings as well as after establishment.  Where development of the building site changed the amount of water reaching the preserved natural resource areas, include appropriate measures for maintaining the natural areas.

  - A schedule for the use of fertilizers appropriate to the plants species, local climate and the pre-establishment and post-establishment needs of the installed landscaping.  Non-organic fertilizers  shall be discontinued following plant establishment.

  - A requirement for a visual inspection of site after all major precipitation events to evaluate systems performance and site impacts.

  - A schedule of maintenance activities of the stormwater management system including, but not limited to, cleaning of gutters, downspouts, inlets and outlets, removal of sediments from pretreatment sedimentation pits and wet detention ponds, vacuum sweeping followed by high-pressure hosing at porous pavement and removal of litter and debris.

  - A schedule of maintenance activities for landcaped areas including, but not limited to, the removal of dead or unhealthy vegetation; reseeding of turf areas; mowing of grass to a height which optimizes lawn health and retention of precipitation.

406.6 Vegetative roofs.  Extensive and intensive vegetative roofs, where provided in accordance with Section 404.3 shall comply with ASTM E2396; ASTM E2397; ASTM E2398 and ASTM E2400 or, shall comply with the following:

- All plantings shall be selected according their United States Department of Agriculture hardiness zone classifications and shall be capable of withstanding the climate conditions of the jurisdiction and the micro climate conditions of the building site including, but not limited to, wind, precipitation and temperature.   Planting density shall provide complete coverage within two years of the date of installation unless a different time period is established in the approved design.  Plants shall be distributed to meet the coverage requirements.  Invasive plant species shall not be planted.  Selected plants shall not add to the potential for fire hazard in the event of severe drought.  There shall be a diversity of types and species of plants.

- The engineered soil medium shall be designed for the physical conditions and local climate to support the plants and shall consist of non-synthetic materials.  The planting design shall provide a wind erosion blanket that protects the engineered soil medium until the plants are established.  The engineered soil medium that shall be not less than 3 inches in depth in all areas.

- All roof penetrations, changes in elevation and parapet walls shall be provided with a non-vegetated buffer not less than 12 inches wide.  Where access to the building facades is provided from locations on the perimeter of the roof, non-vegetated buffers adequate to support associated equipment and to protect the roof shall be provided.

- Plantings shall be managed to maintain the function of the vegetative roof.

SECTION 407

Project electives

407.1 General. Section 407 shall regulate project electives related to natural resource conservation and building site development.  Project electives shall not be mandatory unless selected by the owner or registered design professional and indicated in the Project Elective Checklist required by Section 303.1.

407.2 Preservation of natural resources. Project electives related to the preservation of natural resources shall comply with Sections 407.2.1 through 407.2.7. Development of a building site is permitted to comply with individual electives and to comply with more than one elective. Compliance with multiple electives shall be recognized.

407.2.1 Flood hazard avoidance project elective.  Projects seeking a flood hazard avoidance project elective in accordance with Table 303.1 and Section 303.4 shall comply with this section. Where 25 percent or more of a building site is located within the designated 100 year flood hazard area, all building and site development shall be located on portions of the building site that are not located within the 100 year flood hazard area.  The building site shall not be regraded to raise the elevation of the site to remove areas from the flood hazard area.

407.2.2 Agricultural land project elective.  Where Section 402.2.5 is not listed in Table 302.1 as a mandatory requirement, and where land within the jurisdiction is zoned for agricultural use, development of a building site that is not zoned for agricultural use shall be recognized as a project elective.

402.2.3 Infill site project elective. The development of a building site that is an infill site with a new building and associated site improvements shall be recognized as a project elective.

407.2.4 Brownfield site project elective.  The development of a building site that is a brownfield site with a new building with associated site improvements shall be recognized as a project elective.  The development shall be in accordance with one of the following:

1.	ASTM E1903 Phase II Environmental Assessment; or

2.	Where classified as a brownfield site by a local, state or federal government agency, building and site development shall provide effective remediation approved by the agency which classified the site as a brownfield.

407.2.5 Greenfield development project elective.  Where Section 402.2.6 is not listed in Table 302.1 as a mandatory requirement, and where a new building and associated site improvements are built on a site which is not a greenfield site, compliance with this project elective shall be recognized.  Where the building site meets the criteria of one or more of the exceptions to Section 402.2.6, this project elective shall not be available for selection.

407.2.6 Greenfield proximity to development project elective.  Where Section 402.2.6 is listed in Table 302.2 as a mandatory requirement, and where a building site is a greenfield site located within 1/4 mile distance, measured over roads or designated walking surfaces, of developed residential land with an average density of not less than 16 dwelling units per acre, the development of a building and associated site improvements shall be recognized as a project elective.

407.2.7 Greenfield proximity to diverse uses project elective.  Where Section 402.2.6 is listed in Table 302.1 as a mandatory requirement, and where a building site is a greenfield site located within ¼ mile distance, measured over roads or designated walking surfaces, of not less than 10 diverse uses and within ½ mile distance of not less than 14 diverse uses, the development of a building and associated site improvements shall be recognized as a project elective.  The diverse uses shall include at least two uses from each of the following categories of diverse uses: retail, service and community facility.

407.3 Transportation impact. Project electives related to transportation impact shall comply with Sections 407.3.1 through 407.3.4. Compliance with multiple electives shall be recognized.

407.3.1 Changing and shower facilities project elective.  Where a new building is less than 10,000 square feet in total building floor area, providing changing and shower facilities in accordance with Section 403.2 shall be recognized as a project elective.

407.3.2 Long term bicycle parking and storage project elective.  The development of a new building and associated site improvements where additional long term bicycle parking is provided in accordance with all of the following shall be recognized as a single project elective:

1. 	Provide long term bicycle parking which is twice the number of parking spaces required by Table 403.3;

2. 	Provide spaces in accordance with the Section 403.3.2; and

3. 	Locate not less than 90 percent of long term bicycle parking within a building or provide the parking with a permanent cover including, but not limited to, roof overhangs, awnings, or bicycle storage lockers.

407.3.3 Preferred parking project elective. A project elective shall be recognized where preferred parking for high occupancy, low emission, hybrid or electric vehicles in accordance with Section 403.4 is provided under one of the following conditions:

1. 	Where Section 403.4 is listed in Table 302.1 as a mandatory requirement, and a new building is less than 10,000 square feet in total building floor area.

2. 	Where Section 403.4 is not listed in Table 302.1 as a mandatory requirement.

407.4 Heat island. Project electives related to heat island impact shall comply with Sections 407.4.1 through 407.4.4. Compliance with multiple electives shall be recognized.

407.4.1 Site hardscape project elective 1. In climate zones 1 through 6, as established in International Energy Conservation Code, the development of a new building and associated site improvements where a minimum of 75 percent of the site hardscape shall be in accordance with one or any combination of options in Sections 404.2.1 through 404.2.4, shall be recognized as a project elective.

407.4.2 Site hardscape project elective 2. In climate zones 1 through 6, as established in International Energy Conservation Code the development of a new building and associated site improvements where a minimum of 100 percent of the site hardscape shall be in accordance with one or any combination of options in Sections 404.2.1 through 404.2.4, shall be recognized as a project elective.

407.4.3 Site hardscape project elective 3. In climate zones 7 and 8, as established in International Energy Conservation Code the development of a new building and associated site improvements where a minimum of 50 percent of the site hardscape shall be in accordance with one or any combination of options in Sections 404.2.1 through 404.2.4, shall be recognized as a project elective.

407.4.4 Roof covering project elective. In climate zones 4 through 8, as established in International Energy Conservation Code the development of a new building with roof coverings in accordance with Section 404.3, shall be recognized as a project elective.

407.5 Light pollution reduction elective.  Where Section 405.1 is not listed in Table 302.1 as a mandatory requirement, the development of a new building and associated site improvements in accordance with Section 405.1 shall be recognized as a project elective.

CHAPTER 5

MATERIAL RESOURCE CONSERVATION AND EFFICIENCY

SECTION 501

general

501.1 Scope. The provisions of this chapter shall govern matters related to building material conservation, resource efficiency and environmental performance.

SECTION 502

MATERIAL and waste management

502.1 Construction material and waste management plan. Not less than 35 percent of non-hazardous construction waste shall be diverted from landfills, except where other percentages are indicated in Table 302.1. A Construction Material and Waste Management Plan shall be developed and implemented to recycle or salvage construction materials and waste. The Construction Material and Waste Management Plan shall comply with all of the following:

1. The location where the collection, separation and storage of recyclable construction waste materials such as wood, paper, plastic, aluminum, steel, iron, gypsum board, glass and concrete, shall be indicated.

2. Materials to be diverted from disposal by efficient usage, recycling, reuse on the project, or salvage for future use or sale shall be specified.

3. The amount of materials to be diverted shall be specified and shall be calculated by weight or volume, but not both.

For the purpose of this section, construction and waste materials shall not include land clearing debris, excavated soils and fill and base materials such as, but not limited to, topsoil, sand and gravel. Land-clearing debris shall include trees, stumps, rocks, and vegetation. Excavated soil, fill material and land-clearing debris shall be managed in accordance with Section 402.3.6.

502.2 Post construction waste recycling. Post occupancy recycling areas shall be provided in accordance with one of the following:

1. Building occupant recycling areas shall be designed and constructed in accordance with the jurisdiction’s laws or regulations;

2. Where laws or regulations do not exist or where limited recycling services are available, building occupant recycling areas shall be designed and constructed to accommodate recyclable materials based on the availability of recycling services;

- Where recycling services are not available, building occupant recycling areas shall be designed and constructed to accommodate the future recycling of materials in accordance with an approved design. The approved design shall be based on an analysis of other regional recycling services, laws or regulations.

502.3 Storage of lamps, batteries and electronics. Storage space shall be provided for fluorescent lamps, HID lamps, batteries, electronics, and other discarded items requiring special disposal by the jurisdiction.

SECTION 503

MATERIAL SELECTION

503.1 Material selection and properties. Building materials shall conform to Sections 503.2 and 503.3.

Exceptions:

1. Where life cycle assessment is performed in accordance with Section 304, compliance with Section 503 shall not be required.

2. Electrical and mechanical equipment and controls, plumbing fixtures, fire detection and alarm systems, elevators and conveying systems shall not be required to comply with Section 503.

503.2 Material selection. Not less than 55 percent of the total building materials used in the project, based on mass or cost, shall comply with Section 503.2.1, 503.2.2, 503.2.3, 503.2.4 or 503.2.5. Compliance shall be demonstrated in accordance with those sections singularly or in combination. Each individual material item shall be applied to not more than one section from Sections 503.2.1 through 503.2.5. Materials regulated by Sections 503.2.2, 503.2.3, 503.2.4 and 503.2.5 shall have a design life that is equal to or greater than that indicated in the building service life plan in accordance with Section 505.1.

503.2.1 Used materials.  Used materials shall comply with the provisions for such materials in accordance with the applicable code referenced in Section 102.4 and the applicable requirements of this code.

503.2.2 Recycled content building materials.  Recycled content building materials shall contain not less than 25 percent combined post-consumer and pre-consumer recovered material, and shall comply with Section 503.2.3.

503.2.3. Recyclable building materials.  Building materials shall be manufactured for recyclability with a minimum recovery rate of not less than 30 percent through recycling and reprocessing.

503.2.4 Bio-based materials. Bio-based materials shall be those materials that comply with one or more of the following:

- The bio-based content is not less than 50 percent as determined by testing in accordance with ASTM D6866.

- Wood and wood products used to comply with this section, other than salvaged or reused wood products, shall be labeled in accordance with the SFI Standard, FSC Indicators of Sustainable Forestry, PEFC Council Technical Document or equivalent fiber procurement system.  As an alternative to an on-product label, a Certificate of Compliance indicating conformance with the fiber procurement system shall be permitted. Manufacturer’s fiber procurement systems shall be audited by an accredited third-party.

- The requirements of USDA 7CFR Part 2902.

503.2.5 Indigenous materials.  Indigenous materials or components shall be composed of resources that are recovered, harvested, extracted and manufactured within a 500 mile (800 km) radius of the building site. Where only a portion of a material or product is recovered, harvested, extracted and manufactured within 500 miles (800km), only that portion shall be included. Where resources are transported by water or rail, the distance to the building site shall be determined by multiplying the distance that the resources are transported by water or rail by 0.25, and adding that number to the distance transported by means other than water or rail.

503.3 Environmental stewardship.  At least 75 percent of all building materials shall comply with the requirements of this section. The percentage shall be consistently determined by cost, weight or volume using only one method for the entire project.

503.3.1 Environmental stewardship criteria.  Building materials shall be harvested, extracted, processed, and manufactured at facilities compliant with the clean air, clean water, and pollution prevention regulations of both the country where the materials are harvested, extracted, processed, and manufactured and the country in which the products are used.  In the United States, these regulations are those listed in Items 1 through 4.  For any jurisdiction in which other rules and regulations are applicable, the more stringent of the requirements shall apply.

1. 	Clean air.  United States of America air Pollution Control Act (1955); Clean Air Act (1963); Air Quality Act (1967); Clean Air Act (1972); Clean Air Act Extension (1977); and Clean Air Act (1990).

2. Clean water.  United States of America Federal Water Pollution Control Act (1948); Water Quality Act (1967); Federal water Pollution Control Act (1972); Clean Water Act Amendments (1977); and Clean Water Act Reauthorization (1987).

3. Conservation.  United States of America Resource Conservation and Recovery act (RCRA) (1976) and RCRA Amendments (1984).

4.  Noise control.  United States of America Noise Control Act (1972).

503.3.2 Acceptance.  Acceptance for facilities harvesting, extracting, processing, or manufacturing shall be determined in accordance with one or more of the following:

1. Any facility operating with a legal permit in the United States.

2. Third party evaluation verifiying that the rules and regulations of the country meet or exceed the requirements of the rules and regulations of Section 503.3.1, and evidence is submitted verifying that the facility is legally permitted within that country.

3. Third party evaluation verifying that the specific facility is compliant with the requirements of Section 503.3.1.

SECTION 504

lamps

504.1 Low mercury lamps.  The mercury content in lamps shall comply with Section 504.2 or 504.3.

Exceptions:  Appliance, black light, bug, colored, germicidal, plant, shatter-resistant/shatter-proof/shatter-protected, showcase, suntan, T-8 and T-12 lamps with a color rendering index of 87 or higher, lamps with RDC bases, and lamps used for special-needs lighting for individuals with exceptional needs.

504.2 Straight fluorescent lamps.  Straight, double-ended fluorescent lamps less than 6 feet in nominal length and with bi-pin bases shall contain not more than 5 milligrams of mercury per lamp.

Exception:  Lamps with a rated lifetime greater than 20,000 hours at 3 hours per start operated on an ANSI reference ballast shall not exceed 8 milligrams of mercury per lamp.

504.3 Compact Fluorescent Lamps.  Single-ended pin-base and screw-base compact fluorescent lamps shall contain not more than 5 milligrams of mercury per lamp.

Exception:  Lamps rated at 25 watts or greater shall contain not more than 6 milligrams of mercury per lamp.

SECTION 505

SERVICE LIFE

505.1 Building service life plan. A building service life plan (BSLP) in accordance with this section shall be included in the construction documents.  The design service life shall be not less than 60 years and the BSLP shall indicate the design service life selected for the building.

Exception:  Where justified by community development plans and approved by the code official, a BSLP of 25 years shall be permitted.  A BSLP of 25 years shall be comprised of a dismantling, de-mounting, and re-use plan.

505.1.1 Core, shell and site hardscape components. The Building Service Life Plan (BSLP) shall be based on the Building Service Life Category (BSLC) selected from Table 505.1.1. The design service life of components shall be not less than indicated in Table 505.1.1 for the BSLC selected, except as approved by the code official in cases where practical difficulties are identified in the BSLP. The BSLP shall include a maintenance, repair, and replacement schedule for each component.  Values for component design service life and the maintenance, repair and replacement schedule shall be based on manufacturer’s data or other approved sources and shall be included in the documentation.

Table 505.1.1

BUILDING SERVICE LIFE CATEGORIES AND MINIMUM COMPONENT SERVICE LIFE

| BUILDING DESIGN SERVICE LIFE CATEGORY | 60 Years | 25 Years |
| --- | --- | --- |
| COMPONENT | COMPONENT MINIMUM DESIGN SERVICE LIFE (Years) |
| Structural elements and concealed materials and assemblies | 60 | 25 |
| Materials and assemblies where replacement is cost prohibitive or impractical | 60 | 25 |
| Major materials and assembles that are replaceable | 40 | 25 |
| Mechanical, electrical and plumbing equipment and systems | 25 | 25 |
| Site hardscape | 30 | 25 |

505.1.2 Interior.  A plan to accommodate future re-configuration, dismounting, and disassembly of interior non-loadbearing walls, partitions, lighting and electric systems, suspended ceilings, raised floors, and interior air distribution systems for a minimum of 25 years shall be included in the BSLP. The plan shall verify that the interior materials, components and assemblies have a minimum service life of 25 years, and are adaptable to future reconfigurations within the interior spaces of the building.

SECTION 506

construction phase MATERIAL STORAGE, HANDLING AND MOISTURE CONTROL

506.1 Storage and handling of materials. Materials stored and handled on-site during construction phases shall comply with applicable manufacturer’s recommendations. Where the manufacturer’s recommendations are not available, approved standards or guidelines shall be followed.

506.2 Construction phase moisture control. Porous or fibrous materials and other materials subject to moisture damage shall be protected from moisture during the construction phase. Material damaged by moisture during the construction phase shall be cleaned and dried or, where damage cannot be corrected by such means, shall be removed and replaced.

SECTION 507

PROJECT electives

507.1 General. Section 507 contains project electives related to material resource conservation and efficiency. Project electives shall not be mandatory unless selected by the owner or registered design professional and indicated in the Table 303.1.

507.2 Waste management project elective. Projects seeking a waste management project elective in accordance with Table 303.1 and Section 303.4 shall comply with Section 502.1, except that the materials required to be diverted from landfills shall be increased by 20 percent.

507.3 Material selection project electives. Each of the following shall be considered a separate material selection project elective. The project electives are cumulative and compliance with each item shall be recognized individually.

1. Compliance with this project elective shall require compliance with Section 503.2, except that buildings and structures shall contain used, recycled content, recyclable, bio-based and indigenous materials which comply with Sections 503.2.1 through 503.2.5 such that the aggregate total materials compliant with those sections constitute at least 50 percent of the total building products and materials used, based on mass or cost, used singularly.

2. Same as Item 1 except that such materials shall be used for at least 80 percent of the total mass or cost of materials in the project.

507.4 Multi-story building project electives. Projects seeking multi-story building project electives in accordance with Table 303.1 and Section 303.4 shall comply with this section. The building roof-to- total building floor area and foundation-to- total building floor area ratios shall be reduced by stacking stories. The total occupied space, excluding stairways, shafts, and chases, shall be equal to or exceed the total occupied space determined prior to stacking stories.  Each of the following shall be considered a separate project elective. The project electives are cumulative and compliance with each item shall be recognized individually.

1. The building footprint is reduced by at least 45 percent.

2. The building footprint is reduced by at least 70 percent.

507.5 Reduced building volume project elective. Projects seeking a reduced building volume project elective in accordance with Table 303.1 and Section 303.4 shall comply with this section. The average floor-to-floor and floor-to-roof height of the building, as measured from top of floor to top of floor, and top of floor to the underside of the roof/ceiling portion of the building thermal envelope, shall not exceed the heights indicated in Table 507.5. Calculations shall be made per square foot of the total actual floor area of all rooms and spaces within the building exterior walls that have a minimum ceiling height of 7 feet, including the floor area of atriums and exclusive of stairways, courts and elevator and mechanical shafts.

TABLE 507.5

Maximum AVERAGE Floor to Floor and Floor to Roof Dimensions

| Occupancy Classification | Maximum Height |
| --- | --- |
| Group R | 11‘ 0” |
| All Other Occupancies | 12’ 6” |

507.6 Service life project electives. Service life project electives shall be in accordance with Sections 507.6.1 or 507.6.2.

507.6.1 Building service life plan project electives. Projects seeking building service life plan project electives in accordance with Table 303.1 and Section 303.4 shall comply with this section. A building service life plan (BSLP) in accordance with Section 505.1 shall be included in the construction documents.  BSLP project electives shall be recognized in accordance with the criteria in Table 507.6.1.

TABLE 507.6.1

project Electives for BUILDING SERVICE LIFE CATEGORIES AND

MINIMUM COMPONENT SERVICE LIFE

| project electives | 2 | 1 |
| --- | --- | --- |
| BUILDING DESIGN SERVICE LIFE CATEGORY | 200 Years | 100 Years |
| COMPONENT | COMPONENT MINIMUM DESIGN SERVICE LIFE (Years) |
| Structural elements and concealed materials and assemblies | 200 | 100 |
| Materials and assemblies where replacement is cost prohibitive or impractical | 100 | 100 |
| Major materials and assembles that are replaceable | 40 | 40 |
| Mechanical, electrical and plumbing equipment and systems | 25 | 25 |
| Site hardscape | 75 | 50 |

507.6.2 Interior adaptability project elective:  Projects seeking an interior adaptability project elective in accordance with Table 303.1 and Section 303.4 shall comply with this section. The interior adaptability plan required by Section 505.1.2.2 shall provide for use of at least 75 percent of interior building materials within the same building for a minimum of 35 years.

507.7 Moisture control project elective. Projects seeking a moisture control project elective in accordance with Table 303.1 and Section 303.4 shall comply with this section. Moisture preventative measures shall be inspected in accordance with Sections 902 and 903 for the categories listed in Items 1 through 5. Inspections shall be executed in a method and at a frequency as listed in Table 903.1. Inspections shall be conducted by the registered design professional or an independent inspection agency who shall report to the code official based on the approved pre-determined frequency schedule. Discrepancies shall be brought to the attention of the code official prior to the completion of that work. A final inspection report documenting required testing and corrections of any discrepancies noted in prior inspections shall be submitted at a point in time agreed upon by the code official for purposes of demonstrating compliance.

- Foundation sub-soil drainage system.

- Foundation damp-proofing and water-proofing.

- Flashings: Windows, exterior doors, skylights, wall flashing and drainage systems.

- Exterior wall coverings.

- Roof coverings, roof drainage, and flashings.

CHAPTER 6

ENERGY CONSERVATION, EFFICIENCY AND ATMOSPHERIC QUALITY

SECTION 601

general

601.1 Scope. The provisions of this chapter are designed to reduce energy consumption of buildings.

601.2 Intent. This chapter shall regulate the design, construction, and commissioning of buildings for the effective use of energy. This chapter is intended to provide flexibility to permit the use of innovative approaches and techniques to achieve the effective use of energy.

SECTION 602

ENERGY PERFORMANCE, PEAK POWER AND REDUCED CO2e EMISSIONS

602.1 Total annual net energy use (TANEU).  The building shall be designed and constructed to deliver a total annual net energy use (TANEU) not greater than the values shown in Table 602.1. Buildings complying with the International Energy Conservation Code shall be deemed to have a TANEU of 77.

Table 602.1

Total Annual Net Energy Use by Building Occupancy Type

| Building Occupancy Types | IgCC TANEU Point of Entry IECC a | TANEU of Jurisdictional Choice b |
| --- | --- | --- |
| Assembly: Groups A-1, A-2, A-3, A-4, A-5 | 70 | -- |
| Business: Group B | 70 | -- |
| Educational: Group E | 70 | -- |
| Factory and Industrial: Groups F-1, F-2 | 70 | -- |
| High Hazard: Groups H-1, H-2, H-3, H-4, H-5 | 70 | -- |
| Institutional: Groups I-1, I-2, I-3, I-4 | 70 | -- |
| Mercantile: Group M | 70 | -- |
| Residential: Groups R-1, R-2, {R-3, R-4} | 70 | -- |
| Storage: Groups S-1, S-2 | 70 | -- |
| Utility and Miscellaneous: Group U | 70 | -- |

a. Minimum acceptable performance for all building types and sizes.

b. Where the jurisdiction elects to adopt a greater threshold for energy efficiency, a TANEU of ‘63’ is ten (10) percent better than the IgCC ‘Point of Entry’.  The TANEU of Jurisdictional Choice shall apply only to buildings pursuing performance-based compliance in accordance with Section 602.3.2.

602.2 International Energy Conservation Code.  Buildings shall comply with Sections 502.4, 503.2, 504 and 505 of the International Energy Conservation Code.

602.3 Compliance paths.  Buildings over 25,000 square feet in total building floor area shall comply with Section 602.3.2. All other buildings shall comply with either Section 602.3.1 or Section 602.3.2.

Exception. Alterations shall comply with either Section 602.3.1 or Section 602.3.2

602.3.1 Prescriptive-based compliance. Buildings designed on a prescriptive basis shall comply with the requirements Sections 604, 605, 606, 607, 608, 609, 610, 611 and 612 of this code, and shall be deemed to have a TANEU of 70.

602.3.2 Performance-based compliance. Buildings that are intended to comply on a performance basis shall comply with Sections 604, 605, 609.6, 610, 611 and 612 of this code.

602.3.2.1 Minimum performance.  The building shall be designed and constructed to deliver a total annual net energy use (TANEU) not greater than the value shown in Table 602.1. The TANEU shall be calculated in accordance with Section 603.1.1. Buildings complying with the 2006 International Energy Conservation Code shall be deemed to have a TANEU of 100.

602.3.2.2 Building peak energy demand. Buildings shall be designed and constructed to limit peak energy demand during the building’s anticipated peak consumption period in accordance with Section 603.1.2.

602.3.2.3 Reduced CO2e emissions calculations and reporting. Where reduced CO2e emissions calculations are required in Table 302.1, CO2e emissions calculations shall be performed in accordance with Sections 603.1.3 and 603.1.4. The emissions reduced by the proposed design, as compared to the standard reference design, shall be reported as determined in accordance with Equation 6-1.

(Equation 6-1)	CO2e emissions associated with the standard reference design x TANEU of proposed building / 100

602.4 Documentation and verification for existing buildings. Where required by Chapter 10, documentation and verification of energy performance for alterations to existing buildings shall be in accordance with Sections 602.4.1, 602.4.2 or 602.4.3.

602.4.1 Determination of energy savings. A comparison of the energy use and demand patterns of a pre-retrofit, baseline, 12 month period to the projected energy use and demand patterns of the post-retrofit 12 month period shall be performed using a calculation of energy savings from energy conservation measures.

602.4.2 Measurement-based compliance. Measurement-based compliance shall be performed by an approved agency that documents that the energy use of the building after alterations does not exceed the energy use of the building prior to alterations as measured in consistent units of energy.

Exception. Modeling-based compliance by an approved agency using approved software in accordance with ASHRAE 140.

602.4.3 Third-party certification-based compliance. Certification-based compliance shall be performed by an approved agency that by reason of measurement, simulation, comparative studies, or other approved means, documents that the  building as altered does not consume more energy than the building prior to alterations.

SECTION 603

ENERGY USE AND ATMOSPHERIC IMPACTS

603.1 Determination of building annual energy use, peak energy demand and reduced CO2e emissions. Where buildings are designed using the performance-based compliance path in accordance with Section 602.3.2, or are required to report CO2e emissions in accordance with Section 602.3.2.3, the methods for calculating and verifying annual energy use, peak energy demand, and reduced CO2e emissions shall be in accordance with this section.

603.1.1 Annual energy use. The annual energy use shall include all energy used for building functions covered by this code minus any renewable or waste energy covered under Section 603.1.1.1.

In calculating the annual energy use, electric power used by the building shall be converted to consistent units by multiplying the electric power use at the utility meter by the conversion factor in Table 603.1.1(1) based on the location of the building.

In calculating the annual energy use, fossil fuel used by the building shall be converted to consistent units by multiplying the fossil fuel use at the utility meter by the conversion factor in Table 603.1.1(2). The conversion factor for fossil fuels not listed shall be 1.1. Conversion factors for purchased district heating shall be 1.35 for hot water and 1.45 for steam.  The conversion factor for district cooling shall be 0.33 times the value in Table 603.1.1.1(1) based on the eGRID Sub-region in which the building is located.

The amount of annual energy and the percentage of building annual energy use anticipated to be produced from on-site renewable energy sources shall be clearly indicated by the registered design professional on the construction documents along with relevant supporting compliance documentation.

603.1.1.1 TANEU determination. Building total annual net energy use (TANEU) shall be determined in accordance with Section 603.3 and Equation 6-2.

(Equation 6-2)		TANEU = 77 x  (PD - RE - WE) / RD

Where:

PD =	Total annual energy delivered to the proposed design and consumed on site, as determined in accordance with Section 603

RE =	Total annual energy savings from renewable energy derived on site

RD =	Total annual energy used by a standard reference design, determined in accordance with Section 603

WE=	Total annual energy savings from waste energy recovery

PD, RE, RD and WE shall all be expressed in consistent units of energy in accordance with Section 603.1.1.

603.1.2 Peak energy demand. Documentation shall be provided to demonstrate that the proposed design has a peak energy demand not greater than 0.90 times that of the standard reference design.

603.1.3 Annual direct and indirect CO2e emissions associated with on-site electricity. Where emissions calculations are required by the jurisdiction in Table 302.1, the emissions calculations shall be based on electric power for building functions covered by this code minus any renewable or recovered waste energy covered under Section 602.1.2. Emissions associated with electric power use shall be calculated by multiplying the electric power used by the building at the electric utility meter by the CO2e conversion factor in Table 603.1.3 based on the eGRID Sub-region in which the building is located.

603.1.4 Annual direct and indirect CO2e emissions associated with on-site use of non-renewable fuels. Emissions associated with the use of non-renewable fuels such as natural gas, fuel oil and, propane shall be calculated by multiplying the fossil fuel energy used by the building at the utility meter by the national emission factors in Table 603.1.4. Emissions associated with fossil fuels not listed shall be calculated by multiplying the fossil fuel used by the building at the utility meter by 250. Emissions associated with purchased district energy shall be calculated by multiplying the energy used by the building at the utility meter by 150 for hot water and steam, and for district cooling, the factors from Table 603.1.3 based on the eGRID Sub-region in which the building is located.

Table 603.1.1(1)

Electricity Generation Energy Conservation Factors by eGrid Sub Regiona

| eGRID 2007 Sub-region Acronym | eGRID 2007 Sub-region Name | Energy Conversion Factor |
| --- | --- | --- |
| AKGD | ASCC Alaska Grid | 2.97 |
| AKMS | ASCC Miscellaneous | 1.76 |
| ERCT | ERCOT All | 2.93 |
| FRCC | FRCC All | 2.97 |
| HIMS | HICC Miscellaneous | 3.82 |
| HIOA | HICC Oahu | 3.14 |
| MROE | MRO East | 3.40 |
| MROW | MRO West | 3.41 |
| NYLI | NPCC Long Island | 3.20 |
| NEWE | NPCC New England | 3.01 |
| NYCW | NPCC NYC/Westchester | 3.32 |
| NYUP | NPCC Upstate NY | 2.51 |
| RFCE | RFC East | 3.15 |
| RFCM | RFC Michigan | 3.05 |
| RFCW | RFC West | 3.14 |
| SRMW | SERC Midwest | 3.24 |
| SRMV | SERC Mississippi Valley | 3.00 |
| SRSO | SERC South | 3.08 |
| SRTV | SERC Tennessee Valley | 3.11 |
| SRVC | SERC Virginia/Carolina | 3.13 |
| SPNO | SPP North | 3.53 |
| SPSO | SPP South | 3.05 |
| CAMX | WECC California | 2.61 |
| NWPP | WECC Northwest | 2.26 |
| RMPA | WECC Rockies | 3.18 |
| AZNM | WECC Southwest | 2.95 |

1Sources: EPA eGrid2007 version 1.1, 2005 data; EPA eGrid regional gross grid loss factors; EIA Table 8.4a (Sum tables 8.4band 8.4c) and Table 8.2c (Breakout of Table 8.2b), 2005 data.

Table 603.1.1(2)a

U.S. Average Building Fuels Energy

Conversion Factors by Fuel Type

| Fuel Type | Energy Conversion Factor |
| --- | --- |
| Natural Gas | 1.09 |
| Fuel Oil | 1.13 |
| LPG | 1.12 |

Table 603.1.3

Electricity Emission Rate by eGRID Sub-regiona

| eGRID 2007 Sub-region Acronym | eGRID 2007 Sub-region Name | 2005 CO2e Rate (lbs/MWh) |
| --- | --- | --- |
| AKGD | ASCC Alaska Grid | 1270 |
| AKMS | ASCC Miscellaneous | 515 |
| ERCT | ERCOT All | 1417 |
| FRCC | FRCC All | 1416 |
| HIMS | HICC Miscellaneous | 1595 |
| HIOA | HICC Oahu | 1891 |
| MROE | MRO East | 1971 |
| MROW | MRO West | 1957 |
| NYLI | NPCC Long Island | 1651 |
| NEWE | NPCC New England | 999 |
| NYCW | NPCC NYC/Westchester | 874 |
| NYUP | NPCC Upstate NY | 774 |
| RFCE | RFC East | 1224 |
| RFCM | RFC Michigan | 1680 |
| RFCW | RFC West | 1652 |
| SRMW | SERC Midwest | 1966 |
| SRMV | SERC Mississippi Valley | 1094 |
| SRSO | SERC South | 1601 |
| SRTV | SERC Tennessee Valley | 1623 |
| SRVC | SERC Virginia/Carolina | 1220 |
| SPNO | SPP North | 2106 |
| SPSO | SPP South | 1780 |
| CAMX | WECC California | 768 |
| NWPP | WECC Northwest | 958 |
| RMPA | WECC Rockies | 1999 |
| AZNM | WECC Southwest | 1391 |

- Sources:  EPA eGRID2007 Version 1.1, 2005 data; EPA eGrid regional gross grid loss factor

Table 603.1.4

Fossil Fuel Emission Factors

| Emission Rate a, b (lb/MMbtu HHV) | Natural Gas as Stationary Fuel | Fuel Oil as Stationary Fuel | Propane as Stationary Fuel |
| --- | --- | --- | --- |
| CO2e | 137.35 | 200.63 | 162.85 |

a. 1 MMBtu = 1,000,000 Btu = 10 therms.

b. HHV = High Heating Value.  To convert to kg, multiply the pound value by 0.454.

603.2 Documentation procedures. The documentation procedures for establishing the annual energy use of commercial buildings shall be in accordance with Section 506.4 of the International Energy Conservation Code.

603.3 Calculation procedures. The calculation procedures for establishing the annual energy use of commercial buildings shall be in accordance with Section 506.5 of the International Energy Conservation Code, except as required by this section and the modifications to Table 506.5.1(1) of the International Energy Conservation Code.

Table 506.5.1(1) of the International Energy Conservation Code shall be modified as follows:

  - Replace the glazing row in the table with the following:

IECC Table 506.5.1(1)

Specification for the Standard Reference and Proposed Designs

| BUILDING COMPONENT CHARACTERISTICS | STANDARD REFERENCE DESIGN | PROPOSED DESIGN |
| --- | --- | --- |
| Glazing | Area: The proposed glazing area; where the proposed glazing area is less than 40 percent of above-grade wall area. 40 percent of above-grade wall area; where the proposed glazing area is 40 percent or more of the above-grade wall area. U-factor: from Table 502.3 SHGC: from Table 502.3 except that for climates with no requirement (NR) SHGC = 0.40 shall be used Shading is provided on the south, east, and west walls as required by 605.1.3.3. For Greenfield sites, window wall ratio on the north and south walls is two times greater than on the east and west walls. For Greenfield sites, window wall ratio on the north and south walls is two times greater than on the east and west walls. | As proposed As proposed As proposed As proposed As proposed |

  - Add the following rows to the Table.

Table 506.5.1(1)

Specification for the Standard Reference and Proposed Designs

| BUILDING COMPONENT CHARACTERISTICS | STANDARD REFERENCE DESIGN | PROPOSED DESIGN |
| --- | --- | --- |
| Orientation | For Greenfield sites, twice as long on the east-west axis as on the north-south axis. For non-Greenfield sites, As proposed. | As proposed |
| Electrical Power | Voltage drop in branch circuits: 1.5% at design load Voltage drop in feeders: 1.5% at design load Distribution transformer efficiency, in accordance with Tables 609.8.1,1 (1), 609.8.1.1(2), and 609.8.1.1(3) | Voltage drop in branch circuits: 1.5% at design load As proposed As Proposed |

603.3.1 Performance-based compliance.  The performance-based compliance for electrical systems shall be in accordance with Section 603.3.1.1.

603.3.1.1 Electrical system efficiency performance path. Buildings complying with Section 602.7 shall include electrical system efficiency in both the proposed design and the standard reference design in accordance with Equations 6-3, 6-4 and 6-5.

(Equation 6-3)	Power delivered to the building = Power delivered to load / ESE

(Equation 6-4)	ESE	=	∑ (FE1 X FL1/TL) + (FE2 x FL2/TL) + …

(Equation 6-5)	FE1	=	100% - [0.525% + (VDF1 x 0.35) + (100% – TE1)]

ESE	=	total electrical system efficiency, in percent.

FE 1, 2…	=	efficiency of each feeder, in percent.

FL 1, 2…	=	design load on each feeder.

TL	=	total design load on all feeders.

VDF 1, 2…	=	voltage drop of each feeder, in percent, at design load.

TE 1, 2…	=	efficiency of the distribution transformer powering the feeder.

603.4 Qualified software for determinations of annual energy use. Calculation software tools and procedures used to comply with Section 603 shall include the capabilities identified in accordance with Section 506.6 of the International Energy Conservation Code.

603.5 Design professional in responsible charge of building energy simulation. For purposes of this section, and when it is required that documents be prepared by a registered design professional, the code official shall be authorized to require the owner to engage and designate on the building permit application a registered design professional who shall act as the registered design professional in responsible charge of building energy simulation. If the circumstances require, the owner shall designate a substitute registered design professional in responsible charge of building energy simulation who shall perform the duties required of the original registered design professional in responsible charge of building energy simulation. The code official shall be notified in writing by the owner if the registered design professional in responsible charge of building energy simulation is changed or is unable to continue to perform the duties.

SECTION 604

ENERGY METERING, MONITORING AND REPORTING

604.1 Purpose.  Buildings that consume energy shall comply with Section 604. The purpose of this section is to provide requirements that will ensure that buildings are constructed or altered in a way that will provide the capability for their energy use, production and reclamation to be measured, monitored and reported. This includes the design of energy distribution systems so as to isolate load types, the installation of or ability to install in the future meters, devices and a data acquisition system, and the installation of or the ability to provide for public displays and other appropriate reporting mechanisms in the future.

All forms of energy delivered to the building and building site, produced on the building site or in the building and reclaimed at the building site or in the building shall be metered and all energy load types measured in accordance with this Section.

604.1.1 Buildings with Tenants.  In buildings with tenants, the metering required by Section 604.4 shall be collected for the entire building and for each tenant individually. Tenants shall have access to all data collected for their space.

604.2 Intent. The intent of these requirements is to provide for the ongoing meterability, metering, measuring, reporting and display of the energy use, energy demand and emissions associated with the energy use of the whole building and its systems as required in Section 612 and, where required by Section 613.2, to verify ongoing compliance with the provisions of Sections 602 and 603.

604.3 Energy distribution design requirements and load type isolation. Energy distribution systems within, on or adjacent to and serving a building shall be designed such that each primary circuit, panel, feeder, piping system or supply mechanism supplies only one energy use type as defined in Sections 604.3.1 through 604.3.4. The load type served by each supply mechanism shall be clearly designated with the use served, and adequate space shall be provided for installation of metering equipment or other data collection devices, temporary or permanent, to measure these loads. The energy distribution system shall be designed to facilitate the collection of data for each of the building energy use categories in Section 604.4 and for each of the end use categories listed in Sections 604.3.1 through 604.3.4. Where there are multiple buildings on a building site, each building shall comply separately with the provisions of Section 604.

Exception: Buildings designed and constructed such that the total usage of each of the load types described in Sections 604.3.1through 604.3.4 shall be permitted to be measured through the use of installed sub-meters or other equivalent methods as approved.

604.3.1 HVAC system total energy use. This category shall include all energy used to heat, cool, and provide ventilation to the building including, but not limited to, fans, pumps, boiler energy, chiller energy and hot water.

604.3.2 Lighting system total energy use.  This category shall include all interior and exterior lighting used in occupant spaces and common areas.

604.3.3 Energy used for building operations.  This category includes all energy use by vertical transportation systems, automatic doors, motorized shading systems, ornamental fountains and fireplaces, swimming pools, snow-melt systems, and all other building operations.

604.3.4 Miscellaneous loads. Loads other than those specified in Sections 604.3.1 through 604.3.3.

604.4 Energy type metering.  Buildings shall be provided with the capability to determine energy use and peak demand as provided in this section for each of the energy types specified in Sections 604.4.1 through 604.4.7.  Utility energy meters shall be permitted to be used to collect whole building data, but, shall be equipped with a local data port connected to a data acquisition system in accordance with Section 604.5.

604.4.1 Gaseous fuels.  Gaseous fuels including, but not limited to, natural gas, LP gas, coal gas, hydrogen, landfill gas, digester gas and biogas shall be capable of being metered at the building site to determine the gross consumption and peak demand of each different gaseous fuel by the building and each building on a building site. The installation of gas meters and related piping shall be in accordance with the International Fuel Gas Code.

604.4.2 Liquid fuels. Liquid fuels including, but not limited, to fuel oil, petroleum based diesel, kerosene, gasoline, bio diesel, methanol, ethanol and butane shall be capable of being metered at the building site to allow a determination of the gross consumption and peak demand of each liquid fuel use by the building and each building on a building site. The installation of meters and related piping shall be in accordance with the International Mechanical Code.

604.4.3 Solid fuels. Solid fuels including, but not limited to coal, charcoal, peat, wood products, grains, and municipal waste shall be capable of having their use determined at the building site to allow a determination of the gross consumption and peak demand of each solid fuel use by the building and each building on a building site.

604.4.4 Electric power.  Electric power shall be capable of being metered at the building site to allow a determination of the gross consumption and peak demand by the building and each building on a building site. The installation of electric meters and related wiring shall be in accordance with NFPA 70.

604.4.5 District heating and cooling.  Hot water, steam, chilled water, and brine shall be capable of being metered at the building site, or where produced on the building site, to allow a determination of the gross consumption of heating and cooling energy by each building on a building site. Energy use associated with the production of hot water, steam, chilled water or brine shall be determined based on the fuel used.

604.4.6 Combined heat and power.  Equipment and systems with a connected load greater than 125,000 Btu/hr providing combined heat and power (CHP) shall be capable of being metered to allow a determination of the gross consumption of each form of delivered energy to the equipment. The output of CHP shall be metered in accordance with the applicable portions of Section 604 based on the form(s) of output from the CHP.

604.4.7 Renewable and waste energy. Equipment and systems providing energy from renewable or waste energy sources in accordance with Section 603.1.1.1, or from which energy is included in the determination of the building TANEU shall be capable of being metered to allow a determination of the output of such equipment and systems in accordance with sections 604.4.7.1 through 604.4.7.5.

604.4.7.1 Solar electric. Equipment and systems providing electric power through conversion of solar energy directly to electric power shall be capable of being metered such that the peak electric power (kW) provided to the building and its systems or to off-site entities can be determined at 15 minute intervals and the amount of electric power (kWh) provided to the building and its systems can be determined at a minimum of hourly intervals.

604.4.7.2 Solar thermal.  Equipment and systems providing heat to fluids or gases through the capture of solar energy shall be capable of being metered such that the peak thermal energy (Btu/hr) provided to the building and its systems or to off-site entities can be determined at 15 minute intervals and the amount of heat captured (Btu) for delivery to the building and its systems can be determined at a minimum of hourly intervals.

604.4.7.3 Waste heat.  Equipment and systems providing energy through the capture of waste heat shall be capable of being metered such that the amount of heat captured and delivered to the building and its systems can be determined at a minimum of hourly intervals.

604.4.7.4 Wind Power Systems.  Equipment and systems providing electric power through conversion of wind energy directly to electric power shall be capable of being metered such that the peak electric power (kW) provided to the building and its systems or to off-site entities can be determined at 15 minute intervals and the amount of electric power (kWh) provided to the building and its systems can be determined at a minimum of hourly intervals.

604.4.7.5 Other renewable energy electric production systems.  Equipment and systems providing electric power through conversion of other forms of renewable energy directly to electric power shall be capable of being metered such that the peak electric power (kW) provided to the building and its systems or to off-site entities can be determined at 15 minute intervals and the amount of electric power (kWh) provided to the building and its systems can be determined at a minimum of hourly intervals.

604.5 Energy load type sub-metering.  For buildings that are 25,000 square feet in total building floor area and larger, all of the Energy Load Types as defined in Section 604.3 shall be metered through the use of sub-meters or other approved, equivalent methods meeting the capability requirements of section 604.4.

604.5.1 Buildings less than 25,000 square feet. For buildings that are less than 25,000 square feet in total building floor area, the energy distribution system shall be designed and constructed in such a way as to accommodate the future installation of sub-meters and other approved devices in accordance with Section 604.5. This includes, but is not limited to, providing access to distribution lines and ensuring adequate space for the installation of sub-meters and other approved devices.

604.6 Minimum energy measurement and verification.  Meters sub-meters, and other approved devices installed in compliance with Sections 604.4 and 604.5 shall be connected to a data acquisition and management system capable of storing not less than 36 months worth of data collected by all meters and other approved devices and transferring the data in real time to a display as required in Section 604.7.

604.6.1 Annual emissions.  The data acquisition and management system shall be capable of providing the data necessary to calculate the annual CO2e emissions associated with the operation of the building and its systems using the results of annual energy use measured in accordance with Section 604.6. The calculation shall be based on energy measured for each form of energy delivered to the site on an annual basis. Where reporting of emissions is required, it shall be in accordance with Section 603.

604.7 Energy display.  A permanent, readily accessible and visible display shall be provided adjacent to the main building entrance or on a publicly available internet website. The display shall be capable of providing all of the following:

1.	The current energy demand for the whole building level measurements, updated for each fuel type at the intervals specified in 604.4

2.	The average and peak demands for the previous day and the same day the previous year,

3.	The total energy usage for the previous twelve (12) months.

SECTION 605

AUTOMATED DEMAND RESPONSE (AUTO-DR) INFRASTRUCTURE

605.1 Establishing an open and interoperable automated demand response (Auto-DR) infrastructure. Buildings that contain HVAC or lighting systems shall comply with this section. A building energy management and control system (EMCS) shall be provided and integrated with building HVAC systems controls and lighting systems controls to receive an open and interoperable automated demand response (Auto-DR) relay or internet signal. Building HVAC and lighting systems and specific building energy-using components shall incorporate preprogrammed demand response strategies that are automated with a demand response automation internet software client.

Exception: Buildings located where the electric utility or regional Independent System Operator (ISO) or Regional Transmission Operator (RTO) does not offer a demand response program to buildings covered by this code.

605.2 Software clients. Demand response automation internet software clients shall be capable of communicating with a demand response automation server (DRAS).

605.3 Heating ventilating and air-conditioning (HVAC) systems. The Auto-DR strategy for HVAC systems shall be capable of reducing the building peak cooling HVAC demand by at least 25 percent when signaled from the electric utility, regional Independent System Operator (ISO) or Regional Transmission Operator (RTO), through any combination of the strategies and systemic adjustments, including, but not limited to the following:

1.	Space temperature setpoint reset.

2.	Increasing chilled water supply temperatures.

3.	Increasing supply air temperatures for VAV systems.

4.	Limiting capacity of HVAC equipment that has variable or multiple stage capacity control;

5.	Cycling of HVAC equipment or turning off non-critical equipment;

6.	Disabling HVAC in unoccupied areas.

7.	Limiting the capacity of chilled water and refrigerant control valves.

8.	Limiting the capacity of supply and exhaust fans.

9.	Limiting the capacity of chilled water supply pumps.

10.	Anticipatory control strategies to pre-cool in anticipation of a peak event.

605.3.1 Rebound avoidance. The Auto-DR strategy shall include logic to prevent a rebound peak. When the signal for Auto-DR is ended, a gradual return to normal HVAC equipment operations shall be part of the Auto-DR strategy, through any combination of the strategies and systemic adjustments, including, but not limited to the following:

1.	If close to the unoccupied period, the Auto-DR period shall be extended using a rebound avoidance, extended Auto-DR control strategy until the initiation of the unoccupied period.

2.	Rebound avoidance, slow recovery control strategies, gradually increasing space temperature setpoints or a variance in the timing by cooling zone.

3.	Rebound avoidance, slow recovery control strategies, gradually increasing zone supply air temperatures.

4.	Rebound avoidance, slow recovery control strategies, gradually increasing chilled water temperatures.

5.	Rebound avoidance, sequential equipment recovery strategies, gradually restoring demand limited equipment capacity.

6.	Rebound avoidance, sequential equipment recovery strategies, gradually restoring equipment that was turned off during the Auto-DR period.

7.	Rebound avoidance, slow recovery control strategies, gradually increasing capacity for air moving and pumping systems.

8.	Rebound avoidance, sequential equipment recovery or rebound avoidance, slow recovery control where chilled water and other capacity control valves are sequentially or gradually allowed to return to normal operation, respectively.

605.4 Lighting. The Auto-DR system shall be capable of reducing total connected power of lighting in Group B, office spaces by not less than 30 percent.

Exceptions:

- Police stations, prisons, fire stations, hospitals, and other first-responder facilities.

- Luminaires on emergency circuits.

- Luminaires located in emergency and life safety areas of a building.

- Lighting in buildings that are less than 5,000 square feet in total area.

- Luminaires located within a daylight zone that are dimmable and connected to automatic daylight controls.

605.5 Building component-specific strategies. The Auto-DR system shall be capable of reducing the aggregate electric loads associated with miscellaneous building equipment by not less than 25 percent through any combination of the demand shedding methods specified in Sections 605.5.1 through 605.5.6.

605.5.1 Ornamental fountain pumps. Building equipment shall have the capability to cycle on and off exterior and interior fountain pumps during an Auto-DR curtailment.

605.5.2 Supermarket refrigerated and freezer display cases. Building equipment  shall have the capability to cycle on and off the anti-sweat heaters of refrigerated and freezer display cases during an Auto-DR curtailment.

Exceptions:

- Refrigerated and freezer display case anti-sweat heaters controlled by a humidistat.

- Refrigerated and freezer display case anti-sweat heaters in building equipped with a dehumidification system.

605.5.3 Electric vehicle chargers. Electric vehicle chargers shall be capable of shutting off or ramping down to trickle-charge mode.

Exception: Electric vehicle charger systems designed to take advantage of time-of-use rates during normal operation.

605.5.4 Commercial, manufacturing, industrial process loads. The registered design professional shall identify process equipment loads capable of being shut-off during an AUTO-DR curtailment period without spoiling the process or product quality.

605.5.4.1 Cold storage. Refrigeration loads for cold storage shall be shed during an AUTO-DR curtailment period by increasing the storage temperature setpoints or by unloading chillers.

605.5.5 Elevator and escalator cycling. Where four or more elevators in a single bank serve the same floors of a building, the elevator operating system shall be capable of parking at least two of the elevators in a low-power mode during the Auto-DR curtailment period after all passengers have disembarked these elevators. Where two or more pairs of co-located up and down escalators serve the same floors of a building, the escalator operationg system shall be capable of stopping at least one pair of the escalators in a low-power mode during the Auto-DR curtailment period once passengers are no longer on these escalators.

605.5.6 Irrigation water pumps. Water delivery systems that have large-scale storage water tanks shall be capable of being shut off during an Auto-DR curtailment period. A water measurement system interlocked with the pump control shall be installed such that water supply is available during the Auto-DR curtailment period.

SECTION 606

BUILDING ENVELOPE SYSTEMS

606.1 Prescriptive Compliance. Where buildings are designed using the prescriptive-based compliance path in accordance with Section 602.3.1, building thermal envelope systems shall comply with the provisions of the International Energy Conservation Code for such systems and the provisions of this section.

606.1.1 Insulation and fenestration criteria. The building thermal envelope shall meet the requirements of Table 606.1.1 noted below, based on the climate zone specified in the International Energy Conservation Code. Commercial buildings or portions of commercial buildings enclosing Group R occupancies shall use the R-values from the “Group R” column of Table 606.1.1, as applicable. Commercial buildings or portions of commercial buildings enclosing occupancies other than Group R shall use the R-values from the “All other” column of Table 606.1.1, as applicable. Buildings with a vertical fenestration area or skylight area that exceeds that allowed in Table 606.1.1 shall comply with  Section 506 of the International Energy Conservation Code provided that Sections 502.4, 503.2, 504, 505.2, 505.3, 505.4, 505.6 and 505.7 are satisfied.

606.1.2 U-factor alternative. An assembly with a U-factor, C-factor, or F-factor equal or less than that specified in Table 606 shall be permitted as an alternative to the R-value in Table 606.1.1, as applicable. Commercial buildings or portions of commercial buildings enclosing Group R occupancies shall use the U-factor, C-factor, or F-factor from the “Group R” column of Table 606, as applicable. Commercial buildings or portions of commercial buildings enclosing occupancies other than Group R shall use the U-factor, C-factor or F-factor from the “All other” column of Table 606.1.1, as applicable.

606.1.3 Fenestration. Fenestration shall comply with Table 606.1.1, based on the climate zone specified in the International Energy Conservation Code.

606.1.3.1 Maximum area. The vertical fenestration area, not including opaque doors, shall not exceed the percentage of the gross wall area specified in Table 606.1.1 based on the climate zone specified in the International Energy Conservation Code. The skylight area shall not exceed the percentage of the gross roof area specified in Table 606.1.1.

606.1.3.2 Maximum U-factor and SHGC. For vertical fenestration, the maximum U-factor and solar heat gain coefficient (SHGC) shall be as specified in Table 606.1.1, based on the window projection factor. For skylights, the maximum U-factor and solar heat gain coefficient (SHGC) shall be as specified in Table 606.1.1.

606.1.3.3 Permanent shading devices for fenestration. Vertical fenestration within 45 degrees of the nearest west, south, and east cardinal ordinate shall be shaded by permanent horizontal exterior projections with a projection factor greater than or equal to 0.25.  Where different windows or glass doors have different projection factor values, they shall each be evaluated separately, or an area-weighted projection factor value shall be calculated and used for all windows and glass doors.  Horizontal projections shall extend laterally beyond the edge of the glazing at least one-half of the height of the glazing, except at building corners.

Exceptions:

- Buildings located in hurricane-prone regions in accordance with Section 1609.2 of the International Building Code or on any other building with a mean roof height exceeding that permitted by Table 1504.8 of the International Building Code based on the exposure category and basic wind speed at the building site.

- Windows located in a building wall that is within 18 inches of the lot line.

- Where equivalent shading of the fenestration is provided by buildings, structures, geological formations, or permanent exterior projections that are not horizontal, as determined by sun angle studies at the peak solar altitude on the spring equinox, and three hours before and after the peak solar altitude on the spring equinox.

606.1.4 Air leakage. Air leakage mitigation measures shall be provided in accordance with this section.

606.1.4.1 Sealing of the building envelope. The building thermal envelope shall be durably sealed to limit infiltration. The sealing methods between dissimilar materials shall allow for differential expansion and contraction. The following shall be caulked, gasketed, and weather-stripped and additionally sealed with an air barrier film or approved solid material in accordance with Section 606.1.4.1.1.

- All joints, seams and penetrations.

- Site-built windows, doors and skylights.

- Openings between window and door assemblies and their respective jambs and framing.

- Utility penetrations.

- Dropped ceilings or chases adjacent to the building thermal envelope.

- Knee walls.

- Walls and ceilings separating unconditioned spaces from conditioned spaces.

- Behind tubs and showers on exterior walls.

- Common walls between dwelling units.

- Roof access openings.

- Spandrel areas and junctions.

- Electrical and phone boxes on exterior walls except where the air barrier extends behind boxes or air-sealed-type boxes are installed.

- HVAC register boots that penetrate the building thermal envelope except where sealed to subfloor or drywall.

- Other sources of infiltration.

- Where lighting fixtures with ventilation holes or other similar objects penetrate the continuous air barrier, provisions shall be made to maintain the integrity of the continuous air barrier.

606.1.4.1.1 Air barrier installation. The air barrier material shall be installed, free from holes and breaks, over all exterior walls. Where joints occur horizontally, the upper layer shall be lapped over the lower layer not less than 2 inches (51 mm). Where joints occur vertically, the layers shall be lapped not less than 6 inches (152 mm). The air barrier material shall be continuous to the top of walls, terminated at penetrations and building appendages, and taped in accordance with manufacturer’s installation instructions.

606.1.4.2 Testing requirement. The building envelope tightness shall be considered acceptable where tested air leakage is less than 2.0 CFM/FT2 [0.1094] m3/hr/m2 when tested at a pressure of 33.5 psf (50 Pa). Testing shall occur after rough-in and after installation of penetrations of the building envelope, including penetrations for utilities, HVAC, plumbing, and electrical equipment and appliances.

606.1.4.3 Outdoor air intakes and exhaust openings. Stair and elevator shaft vents and other outdoor air intakes and exhaust openings integral to the building envelope shall comply with Section 502.4.5 of the International Energy Conservation Code without exception.

606.1.4.4 Fireplaces. Wood-burning masonry fireplaces shall be provided with combustion air directly from the outdoors and with a means to tightly close off the chimney flue and combustion air outlets when the fireplace is not in use.

606.1.4.5 Vestibules. Doors that separate conditioned space from the exterior shall be protected with an enclosed vestibule, with all doors opening into and out of the vestibule equipped with self-closing devices. Vestibules shall be designed so that in passing through the vestibule it is not necessary for the interior and exterior doors to open at the same time.

Exceptions:

- Doors to mechanical or electrical equipment rooms.

- Doors opening directly from a sleeping unit or dwelling unit.

- Revolving doors.

- Doors used primarily to facilitate vehicular movement or material handling and adjacent personnel doors.

TABLE 606.1.1

PRESCRIPTIVE BUILDING THERMAL ENVELOPE REQUIREMENTS

a In Sky Type ‘C’ locations (Figure 608.5) the building roof area for skylights shall not to exceed five percent.

## SECTION 607

## BUILDING MECHANICAL SYSTEMS

607.1 Prescriptive compliance.   Where buildings are designed using the prescriptive-based compliance path in accordance with Section 602.3.1, building mechanical systems shall meet the provisions of the International Energy Conservation Code for such systems and the provisions of this section.

607.2 HVAC equipment performance requirements.  HVAC equipment shall comply with sections 607.2.1 through 607.2.3.

607.2.1 Equipment covered by Federal standards. Equipment covered by Federal minimum efficiency standards shall meet the minimum efficiency requirements of the International Energy Conservation Code.

607.2.2 Equipment not covered by Federal standards. Equipment not covered by Federal minimum efficiency standards shall meet the minimum efficiency requirements of this section.

607.2.2.1 Geothermal heat pumps. The efficiency of geothermal heat pumps shall meet the provisions of Table 607.2.2.1 based on the applicable referenced test procedure.

607.2.2.2 Multi-stage geothermal heat pumps. The efficiency of multi-stage geothermal heat pumps shall meet the provisions of Table 607.2.2.1 based on the applicable referenced test procedure.

Table 607.2.2.1

Energy-Efficiency Criteria for  Geothermal Heat Pumps

| Product Type | Minimum EER | Minimum COP | Test Procedure |
| --- | --- | --- | --- |
| Water-to-Air Closed loop | 14.1 | 3.3 | ISO 13256-1 |
| Water-to-Air Open loop | 16.2 | 3.6 | ISO 13256-1 |
| Water-to-Water Closed loop | 15.1 | 3.0 | ISO 13256-2 |
| Water-to-Water Open loop | 19.1 | 3.4 | ISO 13256-2 |
| Direct Expansion (DX) or Direct GeoExchange (DGX) | 15.0 | 3.5 | AHRI 870 |

607.2.2.3 Ventilating fans. Ventilating fans shall comply with the requirements of the ENERGY STAR program.

607.2.3 HVAC system controls.  HVAC System Controls shall meet the requirements of the International Energy Conservation Code except as noted herein.

607.2.3.1 Programmable thermostats. Programmable thermostats shall comply with the requirements of the ENERGY STAR Program.

607.3 Ventilation. Ventilation, either natural or mechanical, shall be provided in accordance with Chapter 4 of the International Mechanical Code. Where mechanical ventilation is provided, the system shall provide the capability to reduce the outdoor air supply to the minimum required by Chapter 4 of the International Mechanical Code, or the minimum required by Section 6.3 of ASHRAE 62.1.

607.4 Duct and plenum insulation, sealing and testing.  Supply and return air ducts and plenums, and air handlers and filter boxes shall be insulated and sealed in accordance with the International Energy Conservation Code except as noted herein.

607.4.1 Testing. Joints, longitudinal and transverse seams and connections in ductwork and plenums shall be leak-tested in accordance with the SMACNA HVAC Air Duct Leakage Test Manual and the rate of air leakage (CL) shall be less than or equal to 6.0 as determined in accordance with International Energy Conservation Code Equation 5-2.

607.5 HVAC piping insulation. Piping in HVAC systems shall be thermally insulated in accordance with Table 607.5. Building cavities and interstitial framing spaces shall be large enough to accommodate the combined diameter of the pipe plus the insulation, plus any other objects in the cavity that the piping must cross.

Exceptions:

- Factory-installed piping within HVAC equipment tested and rated in accordance with Section 607.2.

- Piping conveying fluids having a design operating temperature range between 60(F and 105(F.

- Piping conveying fluids not heated or cooled such as roof and condensate drains, cold water supply, and natural gas piping.

- Where heat gain or heat loss will not increase energy usage such as liquid refrigerant piping.

- Piping having an outside diameter or 1 inch or less, associated with strainers, control valves, and balancing valves.

TABLE 607.5

MINIMUM PIPE INSULATION THICKNESSa

| Fluid | Conductivity Btu-in./(h-ft2-F) | Wall Thicknessd of Pipe Insulation Relative to Nominal Pipe Diameter b,c |
| --- | --- | --- |
| Steam | 0.27 – 0.34 | Double |
| Hot Water | 0.22 – 0.29 | Same |
| Chilled Water | 0.22 – 0.28 | Same |

- Piping with a nominal diameter larger than ¼ inch shall be insulated.

- The proportions in this column apply to all nominal pipe diameters greater than ¼ inch and less than or equal to 2 inches. For nominal pipe diameters larger than 2 inches, outside diameter, the minimum wall thickness of the insulation shall be equal to the wall thickness required for 2 inch pipe.

- For insulation outside the stated conductivity range, the minimum thickness shall be determined as follows: T = r[(1 + t/r)K/k – 1].

Where:

T = minimum insulation thickness (in.).

r = actual outside radius of pipe (in.).

t = insulation thickness listed in the table for applicable fluid temperature and pipe size.

K = conductivity of alternate material at mean rating temperature indicated for the applicable fluid temperature (Btu·in./h·ft2·°F)

k = the upper value of the conductivity range listed in the table for the applicable fluid temperature.

- These thicknesses are based on energy efficiency considerations only.

607.6 Economizers. Economizers shall meet the requirements of the International Energy Conservation Code, except as noted herein.

607.6.1 Economizer systems. Each cooling system that has a fan shall include either an air or water economizer meeting the requirements of Section 607.6.1.1 or 607.6.1.2, respectively.

Exception: Economizers are not required for the following.

1.	Individual fan-cooling units with a supply capacity less than the minimum listed in Table 607.6.1(1).

2.	Systems that require filtration equipment in order to meet the minimum ventilation requirements of Chapter 4 of the International Mechanical Code.

3.	In Group I-2, Hospitals, and Group B, Ambulatory health care facilities, where more than 75 percent of the air designed to be supplied by the system is to spaces that are required to be humidified above 35 F dew-point temperature to comply with applicable codes or accreditation standards.  In all other occupancies, where more than 25 percent of the air designed to be supplied by the system is to spaces that are designed to be humidified above 35°F dew-point temperature to satisfy process needs.

4.	Systems that include a condenser heat recovery system that has the capacity to provide sixty percent of the peak heat rejection load at design conditions;

5.	Systems that serve residential spaces where the system capacity is less than five times the requirement listed in Table 607.6.1(1).

6.	Systems that serve spaces having a sensible cooling load at design conditions, excluding transmission and infiltration loads, of less than or equal to transmission and infiltration losses at an outdoor temperature of 60°F.

7.	Systems expected to operate less than 20 hours per week.

8.	Where the use of outdoor air for cooling will affect supermarket open refrigerated casework systems.

9.	Where the cooling efficiency meets or exceeds the efficiency improvement requirements in Table 607.6.1(2).

TABLE 607.6.1(1) ECONOMIZER REQUIREMENTS

| CLIMATE ZONES | ECONOMIZER REQUIREMENT |
| --- | --- |
| 1A, 1B | No requirement |
| 2A, 2B, 3A, 3B, 3C, 4A, 4B, 4C, 5A, 5B, 5C, 6A, 6B, 7, 8 | Economizers on all cooling systems having a capacity ≥ 54,000 Btu/ha |

For SI: 1 British thermal unit per hour = 0.293 W.

a. The total capacity of all systems without economizers shall not exceed 480,000

Btu/h per building, or 20 percent of the building’s air economizer capacity, whichever is greater.

607.6.1.1 Air economizers. Air economizers shall be designed in accordance with Sections 607.6.1.1.1 through 607.6.1.1.4.

607.6.1.1.1 Design capacity. Air economizer systems shall be capable of modulating outdoor air and return air dampers to provide up to 100 percent of the design supply air quantity as outdoor air for cooling.

607.6.1.1.2 Control signal. Economizer dampers shall be capable of being sequenced with the mechanical cooling equipment and shall not be controlled by only mixed air temperature.

Exception: The use of mixed air temperature limit control shall be permitted for systems controlled from space temperature, such as single-zone systems.

607.6.1.1.3 High-limit shutoff. Air economizers shall be capable of automatically reducing outdoor air intake to the design minimum outdoor air quantity when outdoor air intake will no longer reduce cooling energy usage. High-limit shutoff control types for specific climates shall be chosen from Table 607.6.1.1.3(1). High-limit shutoff control settings for these control types shall be those listed in Table 607.6.1.1.3(2).

607.6.1.1.4 Relief of excess outdoor air. Systems shall provide a means to relieve excess outdoor air during air economizer operation to prevent over-pressurizing of the building. The relief air outlet shall be located to avoid recirculation into the building.

TABLE 607.6.1(2)

EQUIPMENT EFFICIENCY PERFORMANCE EXCEPTION FOR ECONOMIZERS

| CLIMATE ZONES | COOLING EQUIPMENT EFFICIENCY IMPROVEMENTa |
| --- | --- |
| 2A | 17% Efficiency Improvement |
| 2B | 21% Efficiency Improvement |
| 3A | 27% Efficiency Improvement |
| 3B | 32% Efficiency Improvement |
| 4A | 42% Efficiency Improvement |
| 4B | 49% Efficiency Improvement |

a  Where a unit is rated with an IPLV, IEER, or SEER, the minimum values for these metrics must be increased by the percentage listed in the table in order to eliminate the required air or water economizer.  Where a unit is rated only with a full load metric such as EER or COP cooling, these metrics must be increased by the percentage shown.

| TABLE 607.6.1.1.3(1) HIGH-LIMIT SHUTOFF CONTROL OPTIONS FOR AIR ECONOMIZERS |
| --- |
| CLIMATE ZONES | ALLOWED CONTROL TYPES | PROHIBITED CONTROL TYPES |
| 1b, 2b, 3b, 3c, 4b, 4c, 5b, 5c, 6b, 7, 8 | Fixed dry bulb Differential dry bulb Electronic enthalpy a Differential enthalpy Dew-point and dry-bulb temperatures | Fixed enthalpy |
| 1a, 2a, 3a, 4a | Fixed enthalpy Electronic enthalpy a Differential enthalpy Dew-point and dry-bulb temperatures | Fixed dry bulb Differential dry bulb |
| All other climates | Fixed dry bulb Differential dry bulb Fixed enthalpy Electronic enthalpy a Differential enthalpy Dew-point and dry-bulb temperatures |  |

- Electronic enthalpy controllers are devices that use a combination of humidity and dry-bulb temperature in their switching algorithm.

| TABLE 607.6.1.1.3(2) HIGH-LIMIT SHUTOFF CONTROL SETTING FOR AIR ECONOMIZERS |
| --- |
| DEVICE TYPE | CLIMATE | REQUIRED HIGH LIMIT (ECONOMIZER OFF WHEN) |
| Fixed dry bulb | 1b, 2b, 3b, 3c, 4b, 4c, 5b, 5c, 6b, 7, 8, 5a, 6a, 7a All other zones | EQUATION | DESCRIPTION |
|  |  | TOA>75°F | Outdoor air temperature exceeds 75°F |
|  |  | TOA>70°F | Outdoor air temperature exceeds 70°F |
|  |  | TOA>65°F | Outdoor air temperature exceeds 65°F |
| Differential dry bulb | 1b, 2b, 3b, 3c, 4b, 4c, 5a, 5b, 5c, 6a, 6b, 7, 8 | TOA>TRA | Outdoor air temperature exceeds return air temperature |
| Fixed enthalpy | All | hOA> 28 Btu/lba | Outdoor air enthalpy exceeds 28 Btu/lb of dry aira |
| Electronic Enthalpy | All | (TOA , RHOA) > A | Outdoor air temperature/RH exceeds the "A" setpoint curveb |
| Differential enthalpy | All | hOA> hRA | Outdoor air enthalpy exceeds return air enthalpy |
| Dew-point and dry bulb temperatures | All | DPOA>55°F or TOA>75°F | Outdoor air dry bulb exceeds 75°F or outside dew point exceeds 55°F (65 gr/lb) |

a.	At altitudes substantially different than sea level, the Fixed Enthalpy limit shall be set to the enthalpy value

at 75°F and 50 percent relative humidity. As an example, at approximately 6000 ft elevation the fixed enthalpy limit is approximately 30.7 Btu/lb.

b.	Setpoint “A” corresponds to a curve on the psychometric chart that goes through a point at approximately 75°F and 40 percent relative humidity and is nearly parallel to dry-bulb lines at low humidity levels and nearly parallel to enthalpy lines at high humidity levels.

607.6.2 Economizer systems for complex HVAC equipment. Economizer systems for complex HVAC equipment shall be designed in accordance with Sections 607.6.2.1 through 607.6.2.4.

607.6.2.1 Design capacity. Water economizer systems shall be capable of cooling supply air by indirect evaporation and providing up to 100 percent of the expected system cooling load at outdoor air temperatures of 50°F dry bulb / 45° wet bulb and below.

Exception: Systems in which a water economizer is used and where dehumidification requirements cannot be met using outdoor air temperatures of 50°F dry bulb/ 45°F wet bulb must satisfy 100 percent of the expected system cooling load at 45°F dry bulb/40°F wet bulb.

607.6.2.2 Maximum pressure drop. Pre-cooling coils and water-to-water heat exchangers used as part of a water economizer system shall either have a water-side pressure drop of less than 15 ft of water or a secondary loop shall be created so that the coil or heat exchanger pressure drop is not seen by the circulating pumps when the system is in the normal cooling non-economizer mode.

607.6.2.3 Integrated economizer control. Economizer systems shall be integrated with the mechanical cooling system and shall be capable of providing partial cooling whether or not additional mechanical cooling is required to meet the remainder of the cooling load.

607.6.2.4 Economizer heating system impact. HVAC system design and economizer controls shall be such that economizer operation does not increase the building heating energy use during normal operation.

Exception: Economizers on VAV systems that cause zone level heating to increase because of reduction in supply air temperature.

607.7 Variable air volume (VAV) fan control. Individual fans with motors of 1.0 horsepower (0.746 kW) or greater shall be one of the following:

1.	Driven by a mechanical or electrical variable speed drive;

2.	Driven by a vane-axial fan with variable-pitch blades; or

3.	Provided with controls or devices that will result in fan motor demand of not more than 30 percent of its design wattage at 50 percent of design airflow when static pressure set point equals one-third of the total design static pressure, based on manufacturer’s certified fan data.

Static pressure sensors used to control VAV fans shall be placed in a position such that the controller set point is not greater than one-third of the total design fan static pressure, except for systems with direct digital control. If this results in the sensor being located downstream of major duct splits, multiple sensors shall be installed in each major branch to ensure that the static pressure can be maintained in each branch.

For systems with direct digital control of individual zone boxes reporting to the central control panel, the static pressure set point shall be reset based on the zone requiring the most pressure. The set point shall be reset lower until one zone damper is wide open.

Exception: Systems without zone dampers are exempt from the static pressure reset requirements.

607.8 Kitchen exhaust systems. Kitchen exhaust systems shall meet the provisions of the International Energy Conservation Code except as noted herein.

607.8.1 Kitchen exhaust systems. Replacement air introduced directly into the exhaust hood cavity shall not exceed 10 percent of the hood exhaust airflow rate. Conditioned supply air delivered to any space containing a kitchen hood shall not exceed the greater of the ventilation rate required to meet the space heating or cooling load or the hood exhaust flow minus the available transfer air from adjacent spaces where available transfer air is considered to be that portion of outdoor ventilation air not required to satisfy other exhaust needs, such as restrooms, and not required to maintain pressurization of adjacent spaces.

Where the total kitchen hood exhaust airflow rate is greater than 5,000 cfm (2360 L/s) each hood shall have a maximum exhaust rate in accordance with Table 607.8.1 and shall meet one of the following:

1. 	At least 50 percent of all replacement air is transfer air that would otherwise be exhausted.

2. 	Demand ventilation system(s) are provided for at least 75 percent of the exhaust air that are capable of at least 50 percent reduction in exhaust and replacement air system airflow rates, including controls necessary to modulate airflow in response to appliance operation and to maintain full capture and containment of smoke, effluent and combustion products during cooking and when idle.

3. 	Listed energy recovery devices with a sensible heat recovery effectiveness of at least 40 percent shall provided for at least 50 percent of the total exhaust airflow.

Where a single hood, or hood section, is installed over appliances with different duty ratings, the maximum allowable flow rate for the hood or hood section shall be based on the requirements for the highest appliance duty rating under the hood or hood section.

Exception: Where at least 75 percent of all the replacement air is transfer air that would otherwise be exhausted.

TABLE 607.8.1

MAXIMUM NET EXHAUST FLOW RATE (CFM PER LINEAR FOOT)

| Type of Hood | Light Duty Equipment | Medium Duty Equipment | Heavy Duty Equipment | Extra Heavy Duty Equipment |
| --- | --- | --- | --- | --- |
| Wall-mounted canopy | 140 | 210 | 280 | 385 |
| Single island | 280 | 350 | 420 | 490 |
| Double island (per side) | 175 | 210 | 280 | 385 |
| Eyebrow | 175 | 175 | Not allowed | Not allowed |
| Backshelf/Passover | 210 | 210 | 280 | Not allowed |

For SI: 1CFM/linear foot (1.55 L/s per meter)

607.9 Laboratory exhaust systems. Laboratory exhaust systems shall meet the provisions of the International Energy Conservation Code except as noted herein.

607.9.1 Laboratory exhaust systems. Buildings with laboratory exhaust systems having a total exhaust rate greater than 5,000 cfm shall be provided at least one of the following features:

1. 	A VAV laboratory exhaust and room supply system capable of reducing exhaust and makeup air flow rates to the minimum required in the International Mechanical Code

2. 	A heat recovery system to precondition makeup air from laboratory exhaust such that the percentage that the exhaust and makeup air flow rates can be reduced from design conditions plus the sensible recovery effectiveness percentage totals at least 50 percent.

3.	Direct makeup auxiliary air supply equal to at least 75 percent of the exhaust air flow rate capable of being heated and cooled to the design temperatures specified in Section 302.1 of the International Energy Conservation Code.

607.10 Control of HVAC in hotel/motel guest rooms. To reduce hotel and motel HVAC energy usage during unoccupied periods, a dedicated, system shall be installed and integrated to control guest room HVAC energy consumption. Such controls shall be designed to raise cooling and lower heating temperature set points by at least 4 ºF (Δ 2 ºC) during unoccupied periods.

Exception:  Group R-1, Hotels and Motels, with fewer than 20 guest rooms.

## SECTION 608

## BUILDING SERVICE WATER HEATING SYSTEMS

608.1 Prescriptive compliance. Where buildings are designed using the prescriptive-based compliance path in accordance with Section 602.3.1 service water heating systems shall meet the provisions of the International Energy Conservation Code for such systems and the provisions of this section.

608.2 Service water heating (SWH) equipment performance requirements.  Service water heating equipment shall comply with Sections 608.2.1 and 608.2.2.

608.2.1 Equipment covered by Federal standards. Equipment covered by Federal minimum efficiency standards shall meet the minimum efficiency requirements of the International Energy Conservation Code.

608.2.2.1 Water heater controls for dwelling units.  All Water heaters installed in dwelling units in buildings covered by this code shall be equipped with external water temperature  thermostat controls.  The controls shall allow the occupant to set the water temperature at a setting that is below 100 ºF and greater than or equal to 50 ºF.

  - Pools, hot tubs and spas. Pools, hot tubs and spas shall meet the efficiency requirements of the International Energy Conservation Code.

608.3.1 Pools in conditioned space.  For pools that are located within the conditioned space, at least 25 percent of the annual energy consumption of pool operation and at least 50 percent of the peak design space heating, ventilation, and cooling requirements for the space in which the pool is located shall be met by at least one of the following:

## An on-site renewable energy system(s)

- A heat recovery system.

  - Snowmelt systems. Snow melt systems shall comply with the requirements of the International Energy Conservation Code. Hydronic systems shall supplement at least 25 percent of the design snow melting total annual consumption measured in Btu/ft2, energy per unit area. Electric systems shall supplement at least 50 percent of the design snow melt peak load demand. These requirements shall be met by one or more of the following:

Exception: Emergency service ingress and egress.

## 1.	An on-site renewable energy system(s)

2.	A heat recovery system.

  - Rough-ins for future solar hot water pre-heat. Plumbing, electrical and control systems shall be designed and constructed in accordance with Sections 608.5.1 and 608.5.2 to provide for the future installation of a solar water heating system that will be capable of providing at least 50 percent of the energy needed for all systems listed below:

1.	Service Water Heating for kitchen, laundry and bathing.

2.	Pool Water Heating.

3.	Spa Water Heating.

4.	Hot Tub Water Heating.

608.5.1 Solar thermal hot water system piping rough-in. Conduit(s), sleeve(s) or other pathway(s) shall be installed for a minimum of two runs of piping from the future site for solar thermal to the location of the service water heating equipment. The conduit(s), sleeve(s) or other pathway(s) shall have internal dimensions large enough to allow the piping and insulation to be easily installed, removed and replaced. The minimum diameter of the piping shall be ¾ inch nominal and the tubing shall be certified to handle sustained temperatures above 180F. Insulation shall be sized in accordance with Section 607.5.

608.5.2 Solar Electric hot water system electrical rough-in. Conduit not less than ¾ inch in size shall be installed from the future site for solar electric to the electric service panel or room that provides the electric service to the water heating equipment that will be served by the solar electric hot water system.  Conduit not less than ¾ inch in size shall be installed to provide for control wiring.

608.5.2.1 Conduit size. Conduit not less than ¾ inch in size shall be installed from the future solar thermal or solar electric site to the location of the service water heating equipment and the storage tank to provide for control wiring.

608.5.2.2 Terminations. Conduits, sleeves and pathways installed in accordance with this section shall terminate near the solar thermal or solar electric sites and shall be readily accessible.

608.5.2.3 Space for future storage tank. Space for a future storage tank shall be identified and reserved. This space shall be large enough to accommodate storage for a solar thermal system sized to provide 50 percent solar fraction, with an area of at least ten square feet.

## 608.6	Waste water energy recovery system.  The following building types shall be provided with a waste water heat recovery system that will preheat all of the incoming water used for all hot water functions by not less than 10 ºF (5.6 C):

## 1.	Group A-2, Restaurants and Banquet halls;

2.	Group F, Laundries;

3.	Group R-1, Boarding houses (transient), Hotels (transient), Motels (transient);

4.	Group R-2 buildings; and

5.	Group A-3, Health Clubs and Spas

6.	Group I-2, Hospitals, Mental hospitals and Nursing homes.

Exception:  Single-story, slab-on grade and single-story, on crawl-space buildings.

608.7 Service water heating piping insulation. Service water heating piping shall be thermally insulated in accordance with Table 607.5. Where hot water distribution piping is installed within attics and crawlspaces, the insulation shall continue to cover the pipe for a distance of at least 6 inches (152 mm) beyond the building thermal envelope.  Where hot water distribution piping is installed within walls, the insulation must completely surround the pipe with at least 1 inch of insulation. Where hot water piping is installed in a wall of insufficient width to accommodate the pipe and insulation levels of Table 607.5, the insulation thickness shall be permitted to have the maximum thickness that the wall can accommodate, but not less than ½-inch thick.

Exceptions:

- Factory-installed piping within service water heating equipment tested and rated in accordance with Section 607.5.

- Piping conveying fluids not heated or cooled such as cold water supply, and natural gas piping.

- Hot water supply piping exposed under sinks, lavatories and similar fixtures.

- Hot water distribution piping buried within blown-in or sprayed roof/ceiling insulation, such as fiberglass or cellulose, where the insulation completely and continuously surrounds the pipe.

608.7.1 Buried piping. Service hot water piping installed within a slab or below grade shall be insulated in accordance with Section 608.7 and shall be placed within a physically protective, waterproof channel or sleeve having internal dimensions large enough such that the piping and insulation can be removed and replaced, and maintain its dimensional integrity during and after construction.

Exception:  Where the insulation manufacturer stipulates that the pipe insulation will maintain its insulating value in underground applications in damp soil where installed according to the manufacturer’s instructions. This exception does not apply to piping that runs under building slabs.

608.8 Circulating hot water systems.  Circulating hot water systems shall be provided with an automatic or readily accessible manual switch to turn off the hot water circulating pump when not in use. Controls that allow continuous, timer, or water temperature-initiated operation of a circulating pump are prohibited. Gravity or thermosyphon circulation loops are prohibited. Pumps on circulating hot water systems shall be activated on demand by either a hard-wired or wireless activation control of one of the following types:

- A normally-open, momentary contact switch.

- Motion sensors that make momentary contact when motion is sensed. After the signal is sent, the sensor shall go into a lock out mode for not less than 5 minutes to prevent sending a signal to the electronic controls while the circulation loop is still hot.

- A flow switch.

- A door switch.

The controls for the pump shall be electronic and operate on the principal of shutting off the pump with a rise in temperature. Electronic controls shall have a lock-out to prevent operation above 105F degrees in the event of failure of the device that senses temperature rise. The electronic controls shall have a lock out mode for not more than 5 minutes that prevents extended operation of the pump if the sensor fails or is damaged.

SECTION 609

BUILDING ELECTRICAL POWER AND LIGHTING SYSTEMS

609.1 General. Where buildings are designed using the prescriptive-based compliance path in accordance with Section 602.3.1, building electrical power and lighting systems shall meet the provisions of the International Energy Conservation Code for such systems and the provisions of Section 609. Where buildings are designed using the performance-based compliance path in accordance with Section 602.3.2, compliance with Section 609.6 shall be required.

609.2 Sleeping unit controls.  Sleeping units in hotels, motels, boarding houses or similar buildings shall have a captive key control at the main room entry that controls all permanently wired luminaires and switched receptacles, except those in the bathroom(s).  Suites shall have a control meeting these requirements at the entry to each room or at the primary entrance to the suite.

Exception:  Sleeping unit controls are not required in sleeping units where all lighting and switched receptacles are controlled by an occupant sensor.

609.2.1 Sleeping unit bathroom controls.  Bathrooms within sleeping units in hotels, motels, boarding houses or similar buildings shall be equipped with occupant sensors that control all permanently wired luminaires.

Exception:  Up to 5 watts of lighting in each bathroom shall be permitted to be connected to the captive key control at the main room entry instead of being connected to the occupant sensor control.

609.3 Interior light reduction controls.  Occupant sensor controls shall be provided to automatically reduce connected lighting power by at least 50 percent during periods when occupants are not present in all of the following locations.

- Corridors and enclosed stairwells

- Storage and stack areas not open to the public.

- Parking garages.

Lighting in means of egress shall not be reduced below lighting levels required by the International Building Code.

Exception: Automatic power reduction shall not be required when occupant sensor controls are overridden by time switch controls that keep lights on continuously during peak occupancy periods.

609.4 Exterior lighting controls.  Exterior lighting shall comply with the requirements of Sections 609.4.1 and 609.4.2.

609.4.1 Exterior light reduction.  Exterior lighting shall be controlled by a time switch and configured so that the total exterior lighting power is automatically reduced by at least 30 percent within two hours after facility operations conclude.

Exception. Exterior lighting controls need not be controlled for the following occupancies and conditions:

- Group H occupancies.

- Group I-3 occupancies.

- Lighting which is connected to occupant sensor controls.

- Lighting within means of egress.

- Solar powered luminaires that are not connected to a centralized power source.

609.4.2 Exterior lighting and signage shutoff.  The lighting of building facades, signage, and landscape features shall be controlled by a time switch and configured so that it automatically shuts off within one hour after facility operations conclude or as established by the jurisdiction. Where facility operations are continuous, decorative lighting of building facades and landscape features shall automatically shut off at midnight.

609.5 Automatic daylight controls.  Automatic daylight controls and minimum fenestration shall be provided in all daylight zones in accordance with Table 609.5, Figure 609.5, and Section 808.

Exceptions. Automatic daylight controls are not required for the following spaces and equipment:

- Spaces with less than 90 watts of lighting installed in the daylight zone.

- Spaces where medical care is directly provided.

- Spaces within dwelling units or sleeping units.

- Metal halide luminaires with lamp wattages not greater than 150 watts.

TABLE 609.5

MINIMUM FENESTRATION

| Sky Type | Minimum effective aperture (percentage) |
| --- | --- |
|  | Side lightinga | Top lighting |
|  | North-facing walls | South-facing walls | East- or west- facing walls |  |
| Ab | 5.0 | 7.0 | 10.0 | 0.8 |
| Bc | 6.0 | 9.0 | 12.0 | 1.3 |
| Cd | 7.0 | 14.0 | 17.0 | 3.0 |

aFacing 45 degrees or less from the four cardinal compass orientations (N, E, S, & W)

bSky Type A – more than 75% mean sunshine, in accordance with the NOAA Annual Mean Sunshine Percentage Table.

cSky Type B – 45% to 75% mean sunshine, in accordance with the NOAA Annual Mean Sunshine Percentage Table.

dSky Type C – less than 45% mean sunshine, in accordance with the NOAA Annual Mean Sunshine Percentage Table

Figure 609.5

NOAA Annual Mean Sunshine Percentage Table by Sky Type

609.6 Plug load controls.  Receptacles and electrical outlets controlled by an occupant sensor or time switch shall be provided in accordance with all of the following:

- In Group B office spaces without furniture systems incorporating wired receptacles, at least one switched receptacle shall be provided for each 50 square feet.

- In Group B office spaces with furniture systems incorporating wired receptacles, at least one switched circuit shall be provided at each electrical outlet used for powering furniture systems.

- In classrooms in Group B and Group E occupancies, at least four switched receptacles shall be provided in each classroom.

- In copy rooms, print shops, and computer labs, not less than one switched receptacle shall be provided for each data jack.

- In spaces with an overhead cabinet above a counter or work surface, not less than one switched receptacle shall be provided for each work surface.

609.6.1 Distribution and marking.  Controlled receptacles and electrical outlets shall be distributed in a reasonably uniform pattern throughout each space.  Controlled receptacles shall be marked to differentiate them from uncontrolled receptacles.

609.6.2 Furniture systems.  Furniture systems incorporating wired receptacles shall include at least two receptacles at each workstation that are connected to a controlled circuit.

609.6.3 Computer office equipment.  Computer monitors, plug in space heaters, air purifiers, radios, computer speakers, coffee makers, fans, and task lights located in spaces with controlled receptacles shall be plugged into controlled receptacles.

609.6.4 Audio and visual systems.  Displays, projectors, and audio amplifiers in Group B and Group E classrooms, conference and meeting rooms, and multipurpose rooms shall be controlled by an occupant sensor.

609.6.5 Water dispensers.  Water dispensers that utilize energy to cool or heat drinking water shall be controlled by time switch controls.

609.6.6 Refrigerator and freezer cases.  Lighting integral to vending machines and refrigerator and freezer cases shall be controlled by an occupant sensor or a time switch.

609.7 	Fuel gas lighting systems.  Fixtures that generate illumination by combustion of fuel gas shall be included in lighting power calculations required under sections 505.5 and 505.6 of the International Energy Conservation Code by converting the maximum rated btu/hr of the luminaire into watts using Equation 6-6.

(Equation 6-6) Wattage Equivalent = Maximum btu/hr rating of the fuel gas lighting system / 3.413.

Exception: Historic buildings in accordance with Section 101.4.2 of the International Energy Conservation Code.

609.8 Electrical system efficiency.  Electrical systems shall comply with Section 609.8.1.

609.8.1 Prescriptive compliance. Prescriptive compliance for electrical systems shall be in accordance with Sections 609.8.1.1 through 609.8.1.3.

609.8.1.1 Transformer efficiency.  Distribution transformers installed on the load side of the service disconnecting means shall comply with the provisions of Tables 609.8.1.1(1), 609.8.1.1(2) and 609.8.1.1(3), the Energy Policy Act of 2005 as applicable.

Exceptions:

- Transformers not covered by the Energy Policy Act of 2005.

- Transformers for special purpose applications, and not used in general purpose applications.

- Transformers with multiple voltage taps where the highest tap is at least 20 percent more than the lowest tap.

- Drive transformers, rectifier transformers, auto-transformers, uninterruptible power supply transformers, impedance transformers, regulating transformers, sealed and non-ventilating transformers, machine tool transformers, welding transformers, grounding transformers, and testing transformers.

609.8.1.2 Voltage drop in feeders.  The voltage drop in feeder conductors shall not exceed 1.5 percent at design load.

609.8.1.3 Voltage drop in branch circuits.  The voltage drop in branch circuit conductors shall not exceed 1.5 percent at design load.

609.9 Exterior Lighting.  All exterior lighting shall comply with Section 505.6 of the International Energy Conservation Code.

609.10 Verification of lamps and ballasts. Prior to issuance of a certificate of occupancy, the field inspector shall confirm the installation of lighting control devices, type and quantity; luminaires, type and quantity; lamps, type, wattage and quantity, and ballasts, type and performance for at least one representative luminaire of each type consistent with the International Energy Conservation Code, the approved construction documents, and where energy modeling is performed in accordance with Section 603. Where a discrepancy is found, energy calculations and any modeling performed in accordance with Section 603 shall be revised and resubmitted.

Table 609.8.1.1(1)

Low-Voltage Dry-Type Distribution Transformers

(Maximum 600 Volt Primary)

| Single Phase | Three Phase |
| --- | --- |
| kVA Rating | Minimum Efficiency (%) | kVA Rating | Minimum Efficiency (%) |
| 15 | 97.7 | 15 | 97.0 |
| 25 | 98.0 | 30 | 97.5 |
| 37.5 | 98.2 | 45 | 97.7 |
| 50 | 98.3 | 75 | 98.0 |
| 75 | 98.5 | 112.5 | 98.2 |
| 100 | 98.6 | 150 | 98.3 |
| 167 | 98.7 | 225 | 98.5 |
| 250 | 98.8 | 300 | 98.6 |
| 333 | 98.9 | 500 | 98.7 |
| -- | -- | 750 | 98.8 |
| -- | -- | 1000 | 98.9 |

- Dry-type distribution transformers are air-cooled, and do not use oil as a coolant.

- All efficiency values for low-voltage transformers are at 35 percent of nameplate-rated load, determined according to the DOE test procedure.  10 CFR Part 431, Sub-part K, Appendix A.

- All efficiency values for medium-voltage transformers are at 50 percent of nameplate-rated load, determined according to the DOE test procedure.  10 CFR Part 431, Sub-part K, Appendix A.

- Basic impulse insulation level (BIL).

Table 609.8.1.1(2)

Medium-voltage, Dry-Type Distribution Transformers

(Maximum 34,500 Volt Primary, Maximum 600 Volt Secondary)

| Single Phase | Three Phase |
| --- | --- |
| kVA Rating | 20-45 kV BIL Minimum Efficiency (%) | 46-95 kV BIL Minimum Efficiency (%) | >96 kV BIL Minimum Efficiency (%) | kVA Rating | 20-45 kV BIL Minimum Efficiency (%) | 46-95 kV BIL Minimum Efficiency (%) | >96 kV BIL Minimum Efficiency (%) |
| 15 | 98.10 | 97.86 | -- | 15 | 97.50 | 97.18 | -- |
| 25 | 98.33 | 98.12 | -- | 30 | 97.90 | 97.63 | -- |
| 37.5 | 98.49 | 98.30 | -- | 45 | 98.10 | 97.86 | -- |
| 50 | 98.60 | 98.42 | -- | 75 | 98.33 | 98.12 | -- |
| 75 | 98.73 | 98.57 | 98.53 | 112.5 | 98.49 | 98.30 | -- |
| 100 | 98.82 | 98.67 | 98.63 | 150 | 98.60 | 98.42 | -- |
| 167 | 98.96 | 98.83 | 98.80 | 225 | 98.73 | 98.57 | 98.53 |
| 250 | 99.07 | 98.95 | 98.91 | 300 | 98.82 | 98.67 | 98.63 |
| 333 | 99.14 | 99.03 | 98.99 | 500 | 98.96 | 98.83 | 98.80 |
| 500 | 99.22 | 99.12 | 99.09 | 750 | 99.07 | 98.95 | 98.91 |
| 667 | 99.27 | 99.18 | 99.15 | 1000 | 99.14 | 99.03 | 98.99 |
| 833 | 99.31 | 99.23 | 99.20 | 1500 | 99.22 | 99.12 | 99.09 |
| -- | -- | -- | -- | 2000 | 99.27 | 99.18 | 99.15 |
| -- | -- | -- | -- | 2500 | 99.31 | 99.23 | 99.20 |

- Dry-type distribution transformers are air-cooled, and do not use oil as a coolant.

- All efficiency values for low-voltage transformers are at 35 percent of nameplate-rated load, determined according to the DOE test procedure.  10 CFR Part 431, Sub-part K, Appendix A.

- All efficiency values for medium-voltage transformers are at 50 percent of nameplate-rated load, determined according to the DOE test procedure.  10 CFR Part 431, Sub-part K, Appendix A.

- Basic impulse insulation level (BIL).

Table 609.8.1.1(3)

Medium-voltage, Liquid-Immersed Distribution Transformers

(Maximum 34,500 Volt Primary, Maximum 600 Volt Secondary)

| Single Phase | Three Phase |
| --- | --- |
| kVA Rating | Minimum Efficiency (%) | kVA Rating | Minimum Efficiency (%) |
| 10 | 98.62 | 15 | 98.36 |
| 15 | 98.76 | 30 | 98.62 |
| 25 | 98.91 | 45 | 98.76 |
| 37.5 | 99.01 | 75 | 98.91 |
| 50 | 99.08 | 112.5 | 99.01 |
| 75 | 99.17 | 150 | 99.08 |
| 100 | 99.23 | 225 | 99.17 |
| 167 | 99.25 | 300 | 99.23 |
| 250 | 99.32 | 500 | 99.25 |
| 333 | 99.36 | 750 | 99.32 |
| 500 | 99.42 | 1000 | 99.36 |
| 667 | 99.46 | 1500 | 99.42 |
| 883 | 99.49 | 2000 | 99.46 |
| -- | -- | 2500 | 99.49 |

- Dry-type distribution transformers are air-cooled, and do not use oil as a coolant.

- All efficiency values for low-voltage transformers are at 35 percent of nameplate-rated load, determined according to the DOE test procedure.  10 CFR Part 431, Sub-part K, Appendix A.

- All efficiency values for medium-voltage transformers are at 50 percent of nameplate-rated load, determined according to the DOE test procedure.  10 CFR Part 431, Sub-part K, Appendix A.

- Basic impulse insulation level (BIL).

SECTION 610

SPECIFIC APPLIANCES AND EQUIPMENT

610.1 General.  This section provides requirements for the efficiency of appliances and equipment installed in the building or on the building site and shall be applicable to buildings using the prescriptive-based compliance path in accordance with Section 602.3.1 and the performance-based compliance path in accordance with Section 602.3.2.  Permanent appliances and equipment shall meet the provisions of Section 610.2, and portable appliances and equipment shall meet the provisions of Section 610.3.

Exception: Appliances and equipment in compliance with Sections 606 through 609 and those listed in Table 610.1 are not required to comply with either Section 610.2 or 610.3

Table 610.1

Appliances and Equipment Covered by Federal Efficiency Standards

| Residential products | Commercial products |
| --- | --- |
| Battery chargersa | Beverage vending machinesa |
| Clothes dryers | Commercial clothes washers |
| Clothes washers | Ice makers |
| Dehumidifiers | Refrigerators and freezers (packaged) |
| Dishwashers | Supermarket refrigerators |
| Refrigerators, refrigerator-freezers, and freezers | Walk-in coolers and freezers |
| Microwave ovensa |  |
| Room air conditioners |  |
| Ranges and ovens |  |

a These products currently have no Federal standard(s). NOTE: U.S. Department of Energy rulemakings are underway or scheduled.

610.2 Permanent appliances and equipment.  Appliances and equipment not exempted in Section 610.1 that are permanently connected to the building energy supply system(s) shall meet the provisions of Sections 610.2.1 through 610.2.5 as applicable. Such appliances and equipment shall be listed and labeled and installed in accordance with the manufacturer’s installation instructions and the provisions and terms of their listing, the International Energy Conservation Code, International Fuel Gas Code, International Mechanical Code, International Plumbing Code and International Building Code, and shall be provided with controls and energy monitoring systems as required by this code.  Compliance shall be documented, verified and approved by the code official during field inspection.

610.2.1 Elevators.  Elevator systems shall comply with sections 610.2.1.1 through 610.2.1.2.3.

610.2.1.1 Lighting. Light sources for the cab interior shall have an efficacy greater than or equal to 50 lumens/watt.

610.2.1.2 Power conversion system.  Power conversion systems for traction elevators shall comply with sections 610.2.1.2.1 through 610.2.1.2.3.  Non-traction elevator systems shall have equivalent efficiency.  Elevators moving for less than 0.5 hours/day are exempt from the power conversion system requirements.

610.2.1.2.1 Motor. Either induction motors with a Class IE2 efficiency rating, as defined by IEC EN 60034-30, or alternative technologies, such as permanent magnet synchronous motors that have equal or better efficiency, shall be used.

610.2.1.2.2 Transmission. Transmissions shall not reduce the efficiency of the combined motor/transmission below that shown for the Class IE2 motor. Gearless machines are assumed to have 100 percent transmission efficiency.

610.2.1.2.3 Drive. Potential energy released during motion shall be recovered.

610.2.1.3 Ventilation.  Cab ventilation fans shall have an efficacy greater than or equal to 3.0 CFM per watt (0.085 m3/min./watt).

610.2.1.4 Standby mode.  When the elevator is stopped, not occupied, and with doors closed, lighting, ventilation, and car displays shall be capable of being de-energized within 5 minutes of stopping, and re-energized prior to opening the doors.  Power will cease to be applied to the door motor after the elevator is stopped, lighting is de-energized, and no one is in the car, and re-energized upon the next passenger arrival. In buildings with multiple elevators serving the same floors, one or more elevators shall switch to sleep, low power, mode during periods of low traffic.

610.2.1.5 Guides.  All elevator car guides shall be of the roller type, in order to reduce frictional energy losses.  Counterweights with sliding guides shall be balanced in order to minimize frictional losses associated with the counterweight guides.

610.2.2 Escalators and moving walkways. Escalators and moving walkways shall comply with Sections 610.2.2.1 through 610.2.2.5.

610.2.2.1 Lighting.  Light sources, including, but not limited to, balustrade lighting, comb-plate lighting and step demarcation lighting, shall have an efficacy of not less than 50 lm/W.

610.2.2.2 Drive system.  The gearbox shall have a rated efficiency greater than or equal to 94 percent at full load.  Either induction motors with a class IE3 efficiency rating, as defined by IEC EN 60034-30, or permanent magnet synchronous motors shall be used.

610.2.2.3 Energy recovery.  Down-running escalators equipped with direct variable frequency drives shall use regenerative drives and return recovered energy to the power grid.

610.2.2.4 Handrails.  Handrails shall use friction-reducing measures, such as, but not limited to, rollers in newels.

610.2.2.5 Standby mode. During standby mode, escalators and moving walkways shall be automatically slowed to not more than 50 percent of nominal speed.  Escalators and moving walkways shall be turned off when the building is unoccupied or outside of facility operations.  In locations where multiple escalators serve the same passenger load, one or more escalators shall have the capability of being turned off in response to reduced occupant traffic.

610.2.3 Commercial food service equipment. Not less than 50 percent of the aggregate rated power allocated to commercial food service equipment shall be ENERGY STAR-eligible food service equipment including, but not limited to, open deep-fat fryers, hot food holding cabinets, reach-in refrigerators and freezers, solid door refrigerators and freezers defined by ENERGY STAR. Steam cookers, dishwashers, griddles, and convection gas and electric ovens, shall be ENERGY STAR qualified.

### 610.2.4 Conveyors. Motors associated with conveyors shall be sized to meet the expected load and designed to run within 90 percent of capacity at all times the conveyor is expected to operate. Conveyor motors shall be provided with sleep mode controls. Two-speed motors and adjustable-speed drives shall be provided where load weights are expected to vary. Readily accessible controls shall be provided to allow for manual shut off of the conveyor when it is not needed.  Conveyor systems shall be designed to use gravity feed when conditions allow and arranged such that long straight runs are provided with as few drives as possible.

610.3 Portable appliances and equipment.  Appliances and equipment not exempted in Section 610.1 and that are not permanently connected to the building energy supply systems shall meet the provisions of Section 610.3.1. Such appliances and equipment shall be listed and labeled, installed in accordance with the manufacturer’s installation instructions, and provided with controls and energy monitoring systems as required by this code. Compliance shall be documented and verified by the approved agency designated by the adopting agency, during the commissioning or operational phase of the building.

610.3.1 ENERGY STAR appliances and equipment. The building owner or, in tenant-occupied buildings, each tenant, shall maintain on site a list of installed portable ENERGY STAR-eligible appliances and equipment indicating the corresponding rated power of each of the following items and whether each such item is an ENERGY STAR-qualified item:

- Residential service appliances, including, but not limited to, humidifiers and room air cleaners.

- Commercial service appliances, including, but not limited to, clothes washers and dryers.

- Consumer electronics, including, but not limited to, battery charging systems, audio and video appliances, cordless phones, digital to analog converters, set top boxes, televisions, and external power adaptors.

- Office machines and equipment, including, but not limited to, computers, copiers, digital duplicators, displays, multi-function devices, network equipment servers, voice-mail systems, fax machines, mailing machines, desktop monitors, printers, scanners and water coolers;

610.3.2 Aggregate rated power. The aggregate rated power of all ENERGY STAR-qualified portable appliances and equipment in the building or, in tenant-occupied buildings, in each tenant space, as identified by Section 610.3.1 shall constitute at least 50 percent of the aggregate rated power of all portable appliances and equipment in the building or tenant space, respectively. Such a list shall be made available to the code official upon request.

SECTION 611

BUILDING RENEWABLE ENERGY SYSTEMS

611.1 Renewable energy systems requirements. Buildings that consume energy shall comply with this section. Each building or surrounding lot or building site where there are multiple buildings on the building site shall be equipped with one or more renewable energy systems in accordance with this section.

Renewable energy systems shall meet the requirements of Section 611.2 for solar photovoltaic systems, or 611.3 for wind systems, or 611.4 for solar water heating systems, or 611.5 for solar thermal systems, or 611.6 for other renewable energy systems, and 611.7 for performance monitoring and metering of these systems as approved by the code official.

Exceptions:

- Buildings or building sites where there are multiple buildings on the building site providing at least two percent of the total estimated annual energy use of the building, or collective buildings on the site, with on-site renewable energy using a combination of renewable energy generation systems meeting the requirements of Section 611.2, 611.3, 611.4, 611.5 or 611.6.

- Where at least four percent of the total annual building energy consumption from renewable generation takes the form of a five-year commitment to renewable energy credit ownership,  confirmed by the code official.

- Where the combined application of on-site generated renewable energy and a commitment to renewable energy credit ownership as confirmed by the code official, totals not less than four percent of the total annual building energy consumption from renewable generation.

611.1.1 Building performance-based compliance. Buildings and surrounding property or building sites when there are multiple buildings on the building site, that seek compliance with this code in accordance with Section 602.3.2, performance-based compliance, shall be equipped with one or more renewable energy systems that have the capacity to provide not less than two percent of the total calculated annual energy use of the building, or collective buildings on the site, with on-site renewable energy in accordance with Section 603.

611.1.2 Building prescriptive compliance. Buildings and surrounding property or building sites when there are multiple buildings on the building site, which seek compliance with this code in accordance with Section 602.3.1, Prescriptive compliance, shall be equipped with one or more renewable energy systems that have the capacity to provide not less than two percent of the total estimated annual energy use of the building, or collective buildings on the building site, with on-site renewable energy by calculation demonstrating that on-site renewable energy production has a rating of at least 1.75 Btu/hr or at least 0.50 watts per square foot of conditioned floor area, and using any single or combination of renewable energy generation systems meeting the requirements of Sections 611.2, 611.3, 611.4, 611.5 or 611.6.

611.2 Solar photovoltaic systems. Solar photovoltaic systems shall be designed, constructed and sized to provide at least two percent of the total estimated annual electric energy consumption of the building, or collective buildings on the building site in accordance with Section 611.1.1 or 611.1.2; or cover an area equal to not less than 30 percent of the gross building roof area. The array size includes any balance of system equipment, panel spacing, access paths, and conduits.

Exceptions. Solar photovoltaic systems are not required at the following locations:

- Building sites with total global insolation levels lower than 4.00 kWh/m2/day as calculated in accordance with SERI TR-642-761.

- Building sites that will be shaded for at least 50 percent of the daylight hours because of trees, buildings or other obstructions.

611.2.1 Installation, location and structural requirements. Solar photovoltaic arrays shall be located on the building, adjacent to the building, or on the building site, and designed and constructed in accordance with accepted engineering practice.

611.2.1.1 Access. Not less than four feet of clearance shall be provided between any portion of a roof mounted solar photvoltaic array and roof mounted equipment, skylights, access hatches and similar building components that could hinder access to the solar photovoltaic array.

611.2.1.2 Structural requirements. Engineering calculations and details demonstrating adequacy of supporting members, including wind uplift effects, shall be provided by the registered design professional.

611.2.1.3 Installation. Solar photovoltaic systems shall be installed by a licensed solar installation contractor and installed in accordance with the terms of their listing and in accordance with the manufacturer’s installation instructions.

611.2.2 Performance verification.  Solar photovoltaic systems shall be tested upon installation to verify that the installed performance meets the design specifications.  A report of the tested performance shall be provided to the building owner.

611.2.3 Additional requirements. Additional requirements for solar photovoltaic systems shall be as follows:

611.2.3.1 Roof waterproofing. Photovoltaic systems shall be installed in such a way as to prevent leaking at connection points.

611.2.3.2 Electrical. Electrical systems associated with a solar photovoltaic system shall be in accordance with NFPA 70.

611.2.3.3 Utility interconnection. Photovoltaic energy systems that connect to the electric utility shall comply with the local rules and codes governing such interconnections.

611.3 Wind energy systems. Wind energy systems shall be designed, constructed and sized to provide not less than two percent of the total estimated annual electric energy consumption of the building, or collective buildings on the building site in accordance with Section 611.1.1 or 611.1.2; or cover the maximum available gross building roof area excluding rooftop or building site obstructions such as skylights, penthouses and trees.

Exception. Wind energy systems are not permitted to be used to comply with section 611.1 for buildings located in areas with average annual wind speeds less than 14.5 mph (6.5 m/s) where measured at the 80m (262 ft.) height or in areas having a wind power classification of Class 3 or less where measured at the 50m (164 ft.) height, in accordance with Figures 611.3(1) through 611.1(5).

611.3.1 Installation, location and structural requirements. Wind energy systems shall be located on the building, adjacent to the building, or on the building site.

611.3.1.1 Roof top set back.  Roof-top wind turbine installations shall be set back from the edge of the building a minimum distance of two times tip height where tip height is defined as the height from the base of the tower to the top of one blade in the 12 o’clock position.

611.3.1.2 Structural requirements. Wind energy structures and parts thereof shall be designed to withstand the minimum loads prescribed by Chapter 16 and Section 3108 of the International Building Code.

611.3.1.3 Installation. Wind energy systems shall be installed by a licensed wind power installation contractor and installed in accordance with the terms of their listing and in accordance with the manufacturer’s installation instructions.

611.3.2 Performance verification.  Wind energy systems shall be tested upon installation and commissioned in accordance with Section 611.3.1 to verify that the installed performance meets the design specifications.  A report of the tested performance shall be provided to the building owner.

611.3.3 Additional requirements. Wind energy systems shall comply with sections 611.3.3.1 and 611.3.3.2:

611.3.3.1 Electrical. Electrical systems associated with a wind energy system shall be in accordance with the NFPA 70.

611.3.3.2 Utility interconnection.  Wind energy systems that connect to the electric utility shall comply with the local rules and codes governing such interconnections.

611.4 Solar water heating equipment. Not less than ten percent of the building’s annual estimated hot water energy usage shall be met by on-site solar water heating equipment.

Exceptions:

- Solar water heating equipment is not required at building sites where solar insolation totals not more than 3.5 (kW/m2/day) in accordance with Table 611.4.

- On site solar water heating equipment is not required where at least five (5) percent of renewable energy credit ownership is confirmed by the code official.

- For the occupancy Groups identified, not less than five percent of the building’s annual estimated hot water energy usage shall be met by on-site solar water heating equipment.

  - Group A-2, restaurants and banquet halls;

  - Group F, laundries;

  - Group R-1, transient boarding houses, hotels and motels;

  - Group R-2 buildings;

  - Group A-3, health clubs and spas

  - Group I-2, hospitals, mental hospitals and nursing homes.

611.5 Renewable energy system performance monitoring and metering. Renewable energy systems shall be metered and monitored in accordance with Sections 611.5.1 and 611.5.2.

611.5.1 Metering. Separately from the building’s electrical meter, renewable energy systems shall be metered to measure the amount of renewable energy generated on the building site in accordance with Section 604.

611.5.2 Monitoring. Renewable energy systems shall be monitored to measure the peak energy generated by the renewable energy systems during the building’s anticipated peak consumption period in accordance with Section 604.

FIGURE 611.4 PHOTOVOLTAIC RESOURCE MAP (kW/m2/day)

SECTION 612

ENERGY SYSTEMS COMMISSIONING AND COMPLETION

612.1 Mechanical systems commissioning and completion requirements.  Buildings that consume energy shall comply with this section. Prior to passing the final mechanical inspection, the registered design professional shall provide evidence of mechanical systems commissioning and completion in accordance with the International Energy Conservation Code and the provisions of this Section.

Drawing notes shall clearly indicate provisions for commissioning and completion requirements in accordance with this section and are permitted to refer to specifications for further requirements. Copies of all documentation shall be given to the owner and made available to the code official upon request in accordance with Sections 612.1.4 through 612.1.6.

612.1.1 Commissioning plan. A commissioning plan shall be developed by a registered design professional or approved agency and shall include as a minimum all of the following items:

- A narrative describing the activities that will be accomplished during each phase of commissioning, including guidance on who accomplishes the activities and how they are completed.

- Equipment and systems to be tested including, but not limited to, the specific equipment, appliances or systems to be tested and the number and extent of tests.

- Functions to be tested including, but not limited to calibrations and economizer controls.

- Conditions under which the test shall be performed including, but not limited to, affirmation of winter and summer design conditions and full outside air.

- Measurable criteria for performance.

612.1.2 Systems adjusting and balancing. HVAC systems shall be balanced in accordance with generally accepted engineering standards. Air and water flow rates shall be measured and adjusted to deliver final flow rates within the tolerances provided in the product specifications. Test and balance activities shall include as a minimum, the provisions of Sections 612.1.2.1 and 612.1.2.2.

612.1.2.1 Air systems balancing. Each supply air outlet and zone terminal device shall be equipped with a means for air balancing in accordance with the International Mechanical Code. Discharge dampers are prohibited on constant volume fans and variable volume fans with motors of 10 hp (18.6 kW) and larger. Air systems shall be balanced in a manner to first minimize throttling losses then, for fans with system power of greater than 1 hp, fan speed shall be adjusted to meet design flow conditions.

Exception: Fans with fan motor horsepower of 1 hp or less.

612.1.2.2 Hydronic systems balancing. Individual hydronic heating and cooling coils shall be equipped with means for balancing and measuring flow. Hydronic systems shall be proportionately balanced in a manner to first minimize throttling losses, then the pump impeller shall be trimmed or pump speed shall be adjusted to meet design flow conditions. Each hydronic system shall have either the capability to measure pressure across the pump, or shall have test ports at each side of each pump.

Exceptions:

- Pumps with pump motors of 5 hp or less.

- Where throttling results in not greater than five percent of the nameplate horsepower draw above that required if the impeller were trimmed.

612.1.3 Functional performance testing.

612.1.3.1 Equipment. Equipment functional performance testing shall demonstrate the installation and operation of components, systems, and system-to-system interfacing relationships in accordance with approved plans and specifications such that operation, function, and maintenance serviceability for each of the commissioned systems is confirmed. Testing shall include all specified modes of control and sequence of operation, including under full-load, part-load and the following emergency conditions:

- Each mode as described in the sequence of operation;

- Redundant or automatic back-up mode;

- Performance of alarms; and

- Mode of operation upon a loss of power and restoration of power.

Exception: Unitary or packaged HVAC equipment listed in International Energy Conservation Code Tables 503.2.3 (1) through (3), that do not require supply air economizers.

612.1.3.2 Controls. HVAC control systems shall be tested to document that control devices, components, equipment, and systems are calibrated adjusted and operate in accordance with the approved plans and specifications. Sequences of operation shall be functionally tested to document that they operate in accordance with the approved plans and specifications.

612.1.3.3 Economizers.  Air economizers shall undergo a functional test to determine that they operate in accordance with manufacturer’s specifications.

612.1.4 Preliminary commissioning report. A preliminary report of commissioning test procedures and results shall be completed and certified by the registered design professional or approved agency and provided to the building owner. The report shall be identified as “Preliminary Commissioning Report” and shall identify all of the following:

- Itemization of deficiencies found during testing required by this section that have not been corrected at the time of report preparation.

- Deferred tests that cannot be performed at the time of report preparation because of climatic conditions.

- Climatic conditions required for performance of the deferred tests.

612.1.4.1 Acceptance. Buildings, or portions thereof, shall not pass the final mechanical inspection until such time as the code official has received a letter of transmittal from the building owner acknowledging that the building owner has received the Preliminary Commissioning Report.

612.1.4.2 Copy. At the request of the code official, a copy of the Preliminary Commissioning Report shall be made available for review.

612.1.4.3 Certification. A certification, signed and sealed by the registered design professional, documenting that the mechanical and service water heating systems comply the International Energy Conservation Code Sections 503 and 504, respectively, shall be provided to the code official.

612.1.5 Completion requirements. The construction documents shall specify that the construction documents described in this Section be provided to the building owner within 90 days of the date  of receipt of the certificate of occupancy.

612.1.5.1 Drawings. Construction documents shall include as a minimum the location of and performance data pertaining to each piece of equipment.

612.1.5.2 Manuals. An operating manual and a maintenance manual in accordance with industry-accepted standards shall be provided and shall include all of the following:

- Submittal data stating equipment size and selected options for each piece of equipment requiring maintenance.

- Manufacturer’s operation manuals and maintenance manuals for each piece of equipment requiring maintenance, except equipment not furnished as part of the building project. Required routine maintenance shall be clearly identified.

- Names and addresses of at least one service agency.

- HVAC controls system maintenance and calibration information, including wiring diagrams, schematics, and control sequence descriptions. Desired or field-determined set-points shall be permanently recorded on control drawings at control devices or, for digital control systems, in programming comments.

- A complete narrative of how each system is intended to operate, including recommended set-points.

612.1.5.3 System balancing report. A written report describing the activities and measurements completed in accordance with Section 612.1.2 shall be provided.

612.1.5.4 Final commissioning report. A complete report of test procedures and results identified as “Final Commissioning Report” shall be provided and all of the following shall include:

- Results of all functional performance tests.

- Disposition of all deficiencies found during testing, including details of corrective measures used or proposed.

- All functional performance test procedures used during the commissioning process including measurable criteria for test acceptance, provided herein for repeatability.

## Exception: Deferred tests that were not performed at the time of report preparation because of climatic conditions.

612.2 Lighting and electrical systems commissioning and completion requirements. Prior to issuance of a certificate of occupancy, the registered design professional shall provide evidence of lighting and electrical systems commissioning and completion in accordance with the International Energy Conservation Code and the provisions of this section.

Drawing notes shall specify the provisions for commissioning and completion requirements in accordance with this section and are permitted to refer to specifications for further requirements. Copies of all documentation shall be given to the owner and made available to the code official upon request in accordance with Sections 612.2.4 and 612.2.5.

612.2.1 Pre-construction documentation, lighting. Construction and owner education documents shall include floor plans, diagrams and notations of sufficient clarity describing the types of, location and operational requirements of all lighting controls including a sequence of operation and intended set points for all dimming systems and automatic daylight controls, demonstrating conformance to the provisions of this code,  relevant laws, ordinances, rules and regulations, as approved by the code official.

612.2.2 Verification.  The approved agency conducting commissioning shall verify that controls have been installed in accordance with the approved construction documents.  Any discrepancies shall be reviewed for compliance with Section 609 and the requirements of sections 502.2, 502.3 and 502.4 of the International Energy Conservation Code.

612.2.3 Commissioning.  Lighting controls shall be commissioned in accordance with this Section.

612.2.3.1 Occupant sensors. It shall be verified that the functional testing in accordance with International Energy Conservation Code Section 505.2.4 has been performed.

612.2.3.2 Automatic daylight controls. Automatic daylight controls shall be commissioned in accordance with all of the following:

1.	It shall be verified that the placement and orientation of each sensor is consistent with  the manufacturer’s installation instructions. If not, the sensor shall be relocated or replaced.

2.	Control systems shall be calibrated to maintain light levels identified in the construction documents;

3.	Prior to calibration of systems controlling dimmable luminaires, all lamps shall be seasoned in accordance with the recommendations of the lamp manufacturer.

4.	Where located inside buildings, calibration of open-loop daylight controls, which receive illumination from natural light only, shall not occur until fenestration shading devices such as blinds or shades have been installed and commissioned;

5.	Calibration of closed-loop daylight controls, that receive illumination from both natural and artificial light, shall not occur until furniture systems and interior finishes have been installed, and any fenestration shading devices such as blinds or shades have been installed and commissioned; and

6.	Calibration procedures shall be in accordance with the manufacturer’s installation instructions.

612.2.3.3 Time switch and programmable schedule controls. Lighting controls installed in accordance with Section 609 shall be programmed. Scheduling shall incorporate weekday, weekend and holiday operating times, including leap year and daylight savings time corrections. It shall be verified that system overrides work and are located in compliance with Section 505.2 of the International Energy Conservation Code.

612.2.3.4 Dimming systems with preset scenes.  For programmable dimming systems it shall be verified that automatic shutoff and manual overrides are working. Prior to programming, all lamps shall have been in operation, at full output, for 100 hours or seasoned in accordance with the lamp manufacturer’s installation instructions, whichever is less.

612.2.4 Post-commissioning documentation. All of the following documentation shall be provided to the owner in accordance with Section 903.

- All settings determined during commissioning activities outlined in Section 612.2.3.

- A narrative describing the intent and functionality of all controls including any capability for users to override a schedule or master command.

- Specification sheets for all lighting equipment and controls.

- Operation manuals for each lighting control device. Required maintenance and maintenance schedules shall be clearly identified. All documentation and instructions necessary for building maintenance personnel to maintain and re-calibrate lighting systems and controls.

- An annual inspection schedule for lighting controls.

- Troubleshooting information for fluorescent dimming systems and the remediation of switching issues such as false-ons and false-offs.

612.2.5 Post occupancy commissioning.  The commissioning activities in Section 612.2.3 shall be repeated 18 months after occupancy. Control devices that are not functioning properly shall be repaired or replaced. Adjustments to calibration settings shall be documented. This documentation shall be provided to the building owner.

612.3 Building envelope systems commissioning and completion requirements. Prior to issuance of a certificate of occupancy, the registered design professional shall provide evidence of building thermal envelope systems commissioning and completion in accordance with the International Energy Conservation Code and the provisions of this section.

Drawing notes shall specify the provisions for commissioning and completion requirements in accordance with this section and are permitted to refer to specifications for further requirements. Copies of all documentation shall be given to the owner and made available to the code official upon request in accordance with Sections 612.3.1 through 612.3.2.

612.3.1 Pre-construction documentation, building thermal envelope. Construction and owner education documents shall indicate the location, nature and extent of the work proposed and show the functional requirements and operation of all building thermal envelope systems demonstrating conformance to the provisions of this code, relevant laws, ordinances, rules and regulations, as approved by the code official.

612.3.2 Verification. The approved agency conducting commissioning shall verify that building thermal envelope systems have been installed in accordance with the approved construction documents.  Any discrepancies shall be reviewed for compliance with requirements of the International Energy Conservation Code and this code.

## SECTION 613

## Jurisdictional requirements & project electives

613.1 General. Section 613 provides jurisdictional requirements and project electives related to energy conservation and efficiency and atmospheric quality. Project electives shall not be mandatory unless selected by the owner or design professional in responsible charge and indicated in the Project Elective Checklist in accordance with Section 303.4.

613.2 Post certificate of occupancy TANEU, energy demand, and CO2e emissions reporting. Where the jurisdiction indicates in Table 302.1 that ongoing post certificate of occupancy TANEU, energy demand and CO2e emissions reporting is required, and where the jurisdiction has indicated in Tables 302.1 and 602.1 that enhanced energy performance in accordance with Section 602.1 or reduced CO2e emissions in accordance with Section 602.4 is required, TANEU, energy demand, and CO2e emissions reporting shall be provided in accordance with this Section.

613.2.1 Purpose. The purpose of this section is to provide for the uniform reporting and display of the total annual net energy use, peak demand for each energy form and emissions associated with building operations and building sites.

613.2.2 Intent. The intent of these requirements is to provide for the ongoing reporting and display of the total annual net energy use, peak energy demand and emissions associated with operation of the building and its systems to document ongoing compliance with the provisions of Sections 602 and 603.

613.2.3 Reporting. Reports in accordance with Sections 613.2.3.1 through 613.2.3.3 shall be generated.

613.2.3.1 Annual net energy use.  The TANEU associated with the operation of the building and the buildings on the site, as determined in accordance with Section 603.1.1, shall be reported by the building owner or the owner’s registered agent to the [insert name of appropriate state or local government agency to be responsible for collecting reported information].

Where there are multiple buildings on a building site, each building shall have its TANEU reported separately. Where there are energy uses associated with the building site other than the buildings on the site, the TANEU for the building site shall be reported separately.

Energy use for the previous year shall cover the complete calendar year and be reported on, or before, March 1st of the following year.

613.2.3.2 Peak monthly energy demand reporting.  The peak demand of all energy forms serving each building and the building site, as determined in accordance with Section 603.1.2, shall be reported by the building owner or the owner’s registered agent to the [insert name of appropriate state or local government agency to be responsible for collecting reported information].

Where there are multiple buildings on a building site each building shall have its energy demand reported separately. Where there are energy uses associated with the building site other than the buildings on the site, the energy demand for the building site shall be reported separately.

Monthly energy demand data for the previous year shall cover the complete calendar year and be reported on, or before, March 1st of the following year.

613.2.3.3 Annual CO2e emissions reporting. The annual emissions associated with the operation of the building and its systems, as determined in accordance with Section 603.1.3, shall be reported by the building owner or the owner’s registered agent to the [insert name of appropriate state or local government agency to be responsible for collecting reported information].

Where there are multiple buildings on a building site each building shall have its annual emissions reported separately. Where there are energy uses associated with the building site other than the buildings on the site, the annual CO2e emissions for the building site shall be reported separately.

Emissions reported for the previous year shall cover the complete calendar year and be reported on, or before, March 1st of the following year.

613.3 TANEU reduction project electives. Project electives for buildings pursuing Performance-based compliance in accordance with Section 602.3.2 shall be in accordance with Sections 613.3.1 through 613.3.10. TANEU reductions shall not be recognized for buildings designed prescriptively in accordance with Section 602.3.1. Building TANEU shall be determined in accordance with Section 603.

613.3.1 Seven point reduction in TANEU.  Building TANEU determined in accordance with Section 603 shall be at least 7 points lower than the maximum value allowed in Section 602.

613.3.2 Fourteen point reduction in TANEU.  Building TANEU determined in accordance with Section 603 shall be at least 14 points lower than the maximum value allowed in Section 602.

613.3.3 Twenty-one point reduction in TANEU.  Building TANEU determined in accordance with Section 603 shall be at least 21 points lower than the maximum value allowed in Section 602.

613.3.4 Twenty-eight point reductions in TANEU.  Building TANEU determined in accordance with Section 603 shall be at least 28 points lower than the maximum value allowed in Section 602.

613.3.5 Thirty-five point reductions in TANEU.  Building TANEU determined in accordance with Section 603 shall be at least 35 points lower than the maximum value allowed in Section 602.

613.3.6 Forty-two point reductions in TANEU.  Building TANEU determined in accordance with Section 603 shall be at least 42 points lower than the maximum value allowed in Section 602.

613.3.7 Forty-nine point reductions in TANEU.  Building TANEU determined in accordance with Section 603 shall be at least 49 points lower than the maximum value allowed in Section 602.

613.3.8 Fifty-six point reductions in TANEU.  Building TANEU determined in accordance with Section 603 shall be at least 56 points lower than the maximum value allowed in Section 602.

613.3.9 Sixty-three point reductions in TANEU.  Building TANEU determined in accordance with Section 603 shall be at least 63 points lower than the maximum value allowed in Section 602.

613.3.10 Seventy point reductions in TANEU.  Building TANEU determined in accordance with Section 603 shall be at least 70 points lower than the maximum value allowed in Section 602.

613.4 Building thermal envelope systems project elective. Buildings seeking a building thermal envelope system project elective in accordance with Table 303.1 and Section 303.4 shall comply with this section.

613.5 Mechanical systems project elective. Mechanical systems project electives for buildings designed prescriptively in accordance with Section 602.3.1 and buildings pursuing Performance-based compliance in accordance with Section 602.3.2 shall be in accordance with Sections 613.5.1 through 613.5.4.

613.5.1 Mechanical equipment. Mechanical equipment shall meet sections 613.5.1.1 through 613.5.1.4 to achieve the mechanical systems project elective:

613.5.1.1 Heating equipment. For heating equipment, the part-load efficiency of the equipment shall be at least 10 percent greater than the part-load efficiencies shown in the applicable tables of Section 606, the International Energy Conservation Code, or ASHRAE 90.1, or the equipment shall meet ENERGY STAR criteria, as applicable.

613.5.1.2 Cooling equipment. For cooling equipment, the part-load efficiency of the equipment shall be at least 10 percent greater than the part-load efficiencies shown in the applicable tables of Section 606, the International Energy Conservation Code, or ASHRAE 90.1, or the equipment shall meet ENERGY STAR criteria.

613.5.1.3 Geothermal heat pumps. Geothermal heat pumps shall meet the provisions of Table 613.5.1.3 based on the applicable referenced test procedure.

613.5.1.4 Multi-stage geothermal heat pumps. The efficiency of multi-stage geothermal heat pumps shall meet the provisions of Table 613.5.1.3 based on the applicable referenced test procedure.

Table 613.5.1.3

Energy-Efficiency Criteria for Geothermal Heat Pumps

| Product Type | Minimum EER | Minimum COP | Test Procedure |
| --- | --- | --- | --- |
| Water-to-Air Closed loop | 14.1 | 3.3 | ISO 13256-1 |
| Water-to-Air Open loop | 16.2 | 3.6 | ISO 13256-1 |
| Water-to-Water Closed loop | 15.1 | 3.0 | ISO 13256-2 |
| Water-to-Water Open loop | 19.1 | 3.4 | ISO 13256-2 |
| Direct Expansion (DX) or Direct GeoExchange (DGX) | 15.0 | 3.5 | AHRI 870 |

613.5.2 Duct Insulation. Ducts shall be insulated to R-8 minimum where located in unconditioned spaces and R-11 minimum where located outside of the building structure. Where located within a building envelope assembly, the duct or plenum shall be separated from the building exterior or unconditioned or exempt spaces by a minimum of R-8 insulation

613.5.3 Duct system testing. Joints, longitudinal and transverse seams and connections in ductwork and plenums shall be leak-tested in accordance with the SMACNA HVAC Air Duct Leakage Test Manual and shall have a rate of air leakage (CL) less than or equal to 12 as determined in accordance with equation 5-2 of the International Energy Conservation Code.

606.5.3.1 Documentation. Documentation shall be furnished by the designer demonstrating that representative sections totaling at least 50 percent of the duct area have been tested and that all tested sections meet the requirements of Section 613.5.3.

613.5.4 Service water heating equipment. Service water heating equipment shall be in accordance with Section 613.5.4.1.

613.5.4.1 SWH efficiency. The efficiency of the service water heating equipment must be at least 10 percent greater than the efficiencies shown in the International Energy Conservation Code and ASHRAE 90.1 or the service water heating equipment shall be ENERGY STAR qualified.

613.6 Passive design project elective. Buildings seeking a passive design project elective in accordance with Section 303.4 shall comply with this Section.

613.6.1 Passive design provisions. The simulation shall prove that not less than forty percent of the energy conserved in the proposed design, as compared to the standard reference design, has been achieved through passive design. Passive heating and cooling shall use strategies including, but not limited to, building orientation, fenestration provisions, material selection, insulation choices, overhangs, shading means, microclimate vegetation and water use, passive cooling towers, natural heat storage, natural ventilation, and thermal mass.

Chapter 7

water resource conservation and efficiency

# SECTION 701

# GENERAL

701.1 Scope. The provisions of this chapter shall establish the means of conserving water used indoors, outdoors and in wastewater conveyance.

SECTION 702

FIXTURES, FITTINGS, EQUIPMENT AND APPLIANCES

702.1 Fitting and fixture consumption. A schedule of plumbing fixtures and fixture fittings shall be provided that demonstrates compliance with all of the following:

1. The maximum water consumption of fixtures and fittings shall comply with the flow rates specified in Table 702.1 for the fixtures and fittings listed therein.

2. The aggregate potable water consumption of fixtures and fittings shall be 20 percent less than the reference value calculated in accordance with Section 702.1.1.

Exceptions: The following fixtures and devices shall not be required to comply with the reduced flow rates of this section.

- Blowout design water closets having a maximum water consumption of 2.8 gallons (10.4 L) per flush.

- Clinical sinks having a maximum water consumption of 4.5 gallons (17 L) per flush.

- Service sinks, bath faucets, pot fillers, laboratory faucets, utility faucets, and other fittings designed primarily for filling operations.

702.1.1 Aggregate fixture and fitting water consumption calculation. The aggregate consumption of all fixtures and fittings shall be calculated in accordance with Tables 702.1.1(1) and 702.1.1(2) for the purpose of demonstrating compliance with the aggregate consumption requirement in Sections 702.1 and 702.1.2. Table 702.1.1(1) is to be used first to calculate the reference water use and Table 702.1.1(2) is then to be used to calculate the required reduction in that reference water use. The percentage of reduction of the total water use shall be calculated in accordance with equation 7-1.

Consumption for each fixture or fitting type = (flow rate) x (duration) x (daily uses per occupant) x (number of occupants). The aggregate fixture and fitting consumption is equal to the sum of the consumption values for each fixture and fitting located in the occupancy.

Percent reduction = [(R-D)/R] x 100                        (Equation 7-1)

Where:

R= Total reference water use determined from Table 702.1.1(1)

D= Total design water use determined from Table 702.1.1(2)

TABLE 702.1

MAXIMUM FIXTURE AND FITTING FLOW RATES

FOR REDUCED WATER CONSUMPTION

| FIXTURE OR FIXTURE FITTING TYPE | MAXIMUM FLOW RATE |
| --- | --- |
| Showerheade | 2.0 gpmb and WaterSense compliant |
| Lavatory faucet-private | 1.5 gpmc and WaterSense compliant |
| Lavatory faucet-public (metered) | 0.25 gpcd |
| Lavatory faucet-public (nonmetered) | 0.5 gpmc |
| Kitchen and bar sink faucets (non-residential) | 2.2 gpmc |
| Urinal | 0.5 gpf and WaterSense compliant or nonwater urinal |
| Water closet | 1.6 gallons per flusha |
| Prerinse Spray Valves | 1.3 gpmc |
| Drinking Fountains (manual) | 0.7 gpmc |
| Drinking Fountains (metered) | 0.25 gpcd |

a. The effective flush volume of a dual-flush water closet is defined as the composite, average flush volume of two reduced flushes and one full flush.

b. Flow rate at a pressure of 80 psi.

c. Flow rate at a pressure of 60 psi.

d. Gallons per cycle

e.	Includes hand showers, body sprays, rainfall panels and jets. Showerhead(s) shall be supplied by automatic compensating valves that comply with ASSE 1016 or ASME A112.18.1/CSA B125.1 and that are specifically designed to function at the flow rate of the showerheads being used.

TABLE 702.1.1(1)

REFERENCE FIXTURE AND SUPPLY FITTING WATER CONSUMPTION

| Plumbing Fixture or Supply Fitting | Flow Rate or Volumeb | Duration | Daily Uses Per Occupant | Occupantsh | Daily Volume Gallon per day |
| --- | --- | --- | --- | --- | --- |
| Shower head a | 2.5 gpme | 5 min. | 1 | Note c |  |
| Lavatory faucet, private | 2.2 gpmd | 0.25 min. | 3 |  |  |
| Lavatory, public (metered) | 0.25 gpcf | 1 cycle | 3 |  |  |
| Lavatory, public (nonmetered) | 0.5 gpmd | 0.25 min. | 3 |  |  |
| Kitchen and bar sink faucets (non-residential) | 2.2 gpmd | 4 min. | 1 |  |  |
| Urinal | 1.0 gpcf | 1 cycle | 2/male |  |  |
| Water closet | 1.6 gpcf | 1 cycle | 1/maleg | males |  |
|  |  |  | 3/female | females |  |
|  | Total Reference Water Use (R) (gal/day) |  |
| For SI: 1 gallon = 3.785 L, 1 gallon per minute = 3.785 L/m, 1 pound per square inch = 6.895 kPa. |

a. A hand-held shower spray is considered to be a showerhead.

b. Consumption tolerances shall be determined from referenced standards.

c. For shower heads, the number of occupants shall be based upon the anticipated number of shower users.

d. Flow at 60 psi

e. Flow at 80 psi

f. Gallons per cycle (gpc)

g. The daily use per male occupant shall be 3 where urinals are not installed

h. The number of occupants shall be that number used to determine the required number of plumbing fixtures in accordance with the International Plumbing Code.

TABLE 702.1.1(2)

DESIGN FIXTURE AND SUPPLY FITTING WATER CONSUMPTION

| Plumbing Fixture or Supply Fitting | Flow Rate or Volumebg | Duration | Daily Uses Per Occupant | Occupants f | Daily Volume Gallon per day |
| --- | --- | --- | --- | --- | --- |
| Shower head a |  | 5 min. | 1 | Note c |  |
| Lavatory faucet, private |  | 0.25 min. | 3 |  |  |
| Lavatory, public (metered) |  | 1 cycle | 3 |  |  |
| Lavatory, public (nonmetered) |  | 0.25 min. | 3 |  |  |
| Kitchen and bar sink faucets (non-residential) |  | 4 min. | 1 |  |  |
| Urinal |  | 1 cycle | 2/male |  |  |
| Water closet d |  | 1 cycle | 1/malee | males |  |
|  |  |  | 3/female | females |  |
|  | Total Design Water Use (D)(gal/day) |  |
| For SI: 1 gallon = 3.785 L, 1 gallon per minute = 3.785 L/m, 1 pound per square inch = 6.895 kPa. |

a. A hand-held shower spray is considered to be a shower head.

b. Consumption tolerances shall be determined from referenced standards.

c. For shower heads, the number of occupants shall be based upon the anticipated number of shower users.

d. Gravity-flush High-Efficiency Water Closets (HETs) shall be certified to the current WaterSense High-Efficiency Toilet Specification.

e.The daily use per male occupant shall be 3 where urinals are not installed.

f. The number of occupants shall be that number used to determine the required number of plumbing fixtures in accordance with the International Plumbing Code.

g. Where non-potable water is supplied to a fixture, enter zero in this column for that fixture.

702.1.2 Additional reductions. The provisions for Tier 1 and Tier 2 maximum fixture flow rates shall be applicable where indicated in Table 302.1. The specific requirements for Tier 1 and Tier 2 fixture and fitting consumption shall be as follows:

Tier 1. A schedule of plumbing fixtures and fixture fittings shall be provided that demonstrates that fixture and fitting consumption meets the applicable reduced flow rates specified in Table 702.1 and that demonstrates a 30 percent reduction in the reference aggregate fixture and fitting potable water consumption calculated in accordance with Section 702.1.1.

Tier 2. A schedule of plumbing fixtures and fixture fittings shall be provided that demonstrates that fixture and fitting consumption  meets the applicable reduced flow rates specified in Table 702.1 and that demonstrates a 40 percent reduction in the reference aggregate fixture and fitting potable water consumption calculated in accordance with Section 702.1.1.

702.1.3 Reduction prohibited. The flow rates for emergency and decontamination fixtures and fittings shall not be reduced below the manufacturer’s specifications.

702.2 Combination tub and shower valves. Tub spout leakage from combination tub and shower valves that occurs when the outlet flow is diverted to the shower shall be not more than 0.1 gpm, measured in accordance with the requirements of ASME A112.18.1/CSA B125.1.

702.3 Food establishment pre-rinse spray heads. Food establishment pre-rinse spray heads shall have a maximum flow rate in accordance with Table 702.1 and shall shut off automatically when released. Pre-rinse spray head valves shall not be equipped with hold-open devices.

702.4 Drinking fountain controls. Drinking fountains equipped with manually controlled valves shall shutoff automatically upon the release of the valve.  Metered drinking fountains shall comply with the flow volume specified in Table 702.1.

702.5 Nonwater urinal connection. The fixture drain for nonwater urinals shall connect to a branch drain that serves one or more lavatories that discharge upstream of such urinals.

702.6 Appliances. Sections 702.6.1 through 702.6.4 shall regulate appliances that are not related to space conditioning.

702.6.1 Clothes washers. Clothes washers shall be Energy Star labeled. Clothes washers in public laundry facilities shall consume not more than 8.0 gallons (30.28 L) of water per cubic foot of clothes container volume per cycle on any wash setting.

702.6.2 Ice makers. Ice makers shall not be water cooled. Ice makers shall comply with the requirements of the Energy Star Program for commercial ice machines.

702.6.3 Food steamers. Food steamers shall consume not more than 2.0 gal (7.5 L) per hour in the full operational mode.

702.6.4 Dishwashers. Dishwashers shall be Energy Star labeled or shall be in accordance with Table 702.6.4.

# TABLE 702.6.4

MAXIMUM WATER CONSUMPTION FOR

COMMERCIAL DISHWASHERS

| DISHWASHER Type | SANITATION METHOD |
| --- | --- |
|  | High Temperature (gallons per rack) | Chemical (gallons per rack) |
| Conveyor | 0.7 | 0.62 |
| Door | 0.95 | 1.16 |
| Under Counter | 0.9 | 0.98 |

702.7 Municipal reclaimed water. Where required by Table 302.1 and where municipal reclaimed water is accessible and allowed for such use by the laws, rules and ordinances applicable in the jurisdiction, it shall be supplied to water closets, water-supplied urinals, water-supplied trap primers and applicable industrial uses.

702.8 Efficient hot water distribution systems. The volume of water in the piping between the source of hot water and the hot water outlets of shower, sink and lavatory fixture fittings shall not exceed 87 ounces. The volume of water contained in fixture branch piping that connects to a hot water circulation loop or electrically heat- traced pipe shall not exceed 32 ounces (0.47 L). The volume shall be calculated in accordance with Section 702.8.2.

702.8.1 Circulating hot water systems.  Circulating hot water systems shall be provided with an automatic or readily accessible manual switch to turn off the hot water circulating pump when not in use.

702.8.2 Volume calculation.  The volume of water between the source of hot water and a given outlet shall be calculated by adding the internal volume of all piping, fittings, valves, meters, and manifolds between the source and the outlet.  Piping volumes shall be calculated using Table 702.8.2.  Where water is supplied by a circulating hot water system or an electrically heat-traced pipe, the hot water source shall be considered to be the loop or the heat -traced pipe, and the volume shall include the fitting on the loop that supplies the fixture branch.

TABLE 702.8.2

INTERNAL VOLUME OF

VARIOUS TYPES OF WATER DISTRIBUTION PIPE AND TUBING

| Nominal Pipe or Tube Size (inch) | PIPE OR TUBING MATERIAL |
| --- | --- |
|  | COPPER (Type) | CPVC | PE | PEX |
|  | M | L | K | CTS SDR 11 | SCH 40 | SCH 80 | AL-PE | CTS SDR 9 | -AL-PEX |
|  | Liquid Ounces per foot of length |
| 3/8 | 1.06 | 0.97 | 0.84 | NA | 1.17 | 0.86 | 0.63 | 0.64 | 0.63 |
| 1/2 | 1.69 | 1.55 | 1.45 | 1.25 | 1.89 | 1.46 | 1.31 | 1.18 | 1.31 |
| 3/4 | 3.43 | 3.22 | 2.90 | 2.67 | 3.38 | 2.74 | 3.39 | 2.35 | 3.39 |
| 1 | 5.81 | 5.49 | 5.17 | 4.43 | 5.53 | 4.56 | 5.56 | 3.91 | 5.56 |
| 1 1/4 | 8.70 | 8.36 | 8.09 | 6.61 | 9.66 | 8.24 | 8.49 | 5.81 | 8.49 |
| 1 1/2 | 12.18 | 11.83 | 11.45 | 9.22 | 13.20 | 11.38 | 13.88 | 8.09 | 13.88 |
| 2 | 21.08 | 20.58 | 20.04 | 15.79 | 21.88 | 19.11 | 21.48 | 13.86 | 21.48 |

702.9 Trap priming water. Potable water shall not be used for trap priming purposes where a municipal reclaimed water distribution system or a graywater distribution system is provided.

702.9.1 Filtration required. Non-potable water utilized by pressurized trap primer devices shall be filtered by a 100 micron or finer filter.

702.9.2 Labeling and signage. Each trap primer device utilizing non-potable water shall be provided with signage in accordance with Section 706.2.

702.10 Makeup water supply.  Onsite non-potable water supply systems, such as on-site reclaimed water, graywater and rain water harvest systems, shall be supplied with municipal-reclaimed makeup water except that potable water shall be supplied where municipal reclaimed water is not accessible or is not allowed for such use by the laws, rules and ordinances applicable in the jurisdiction.

702.11 Water powered pumps.  Water-powered pumps are prohibited.

702.12 Food service handwashing faucets.  Faucets for handwashing sinks in food service preparation and serving areas shall be of the self-closing type.

702.13 Dipper wells.  The water supply to a dipper well shall have a shutoff valve and flow control valve. Water flow into a dipper well shall not exceed 6 gpm (22.7 lpm) at a supply pressure of 60 psi (413.7 kPa).

702.14 Automated vehicle wash facilities.  Not less than 50 percent of the water used for the rinsing phase of the wash cycle at automated vehicle wash facilities shall be collected to be reused for the washing phase. Towel and chamois washing machines  shall have high-level water cut-offs.

702.15 Self-service vehicle wash facilities.  Spray wand nozzles used at self-service vehicle wash facilities shall discharge not more than 3 gpm (11.4 lpm). Faucets for chamois wringer sinks shall be of the self closing type.

702.16 Vehicle washing facilities.  Wastewater from reverse osmosis water treatment systems installed in vehicle washing facilities shall discharge to the washing phase water holding tank.

702.17 Covers.  Spas shall be provided with vapor-retardant covers.  Installed covers shall be in continuous contact with the rim surface of the spa.

702.18 Splash troughs.  Swimming pool splash troughs shall discharge to the pool water system.

702.19 Covers.  Swimming pools shall be provided with vapor-retardant covers.

# SECTION 703

HVAC SYSTEMS AND EQUIPMENT

703.1 Hydronic closed systems. Closed loop hydronic heating and cooling systems, and ground-source heat pump systems shall not be connected to a potable makeup water supply.

703.2 Humidification systems. Humidification systems shall be disabled and locked-out when the relative humidity in the space served is over 55 percent.

space served is 55% and higher.

703.3 Condensate coolers and tempering. Potable water shall not be used to reduce the temperature of waste water such as steam condensate and boiler blow-down water.

703.4 Condensate drainage recovery. Where a non-potable water source, such as a graywater or rain water collection system, is installed on site, or water features or fountains are installed within the building, cooling system condensate shall be collected and discharged to such collection system, water feature or fountain.

703.5 Heat exchangers. Potable water shall not be used as a coolant in any heat exchanger except where the potable water is recirculated.

703.6 Humidifier discharge.  Water discharge from flow-through type humidifiers and from the draining and flushing operations of other types of humidifiers shall be collected for reuse where a collection and reuse system exists.

# SECTION 704

WATER TREATMENT DEVICES AND EQUIPMENT

# 704.1 Water softeners. Water softeners shall comply with Sections 704.1.1 through 704.1.4.

704.1.1 Demand initiated regeneration.   Water softeners shall be equipped with demand- initiated regeneration control systems. Such control systems shall automatically initiate the regeneration cycle after determining the depletion, or impending depletion of softening capacity.

704.1.2 Water consumption. Water softeners shall have a maximum water consumption during regeneration of 5 gal (18.9 L) per 1000 grains of hardness removed as measured in accordance with NSF 44.

704.1.3 Waste connections. Waste water from water softener regeneration shall not discharge to reclaimed water collection systems and shall discharge in accordance with the International Plumbing Code.

704.1.4 Efficiency and listing. Water softeners that regenerate in place, that are connected to the water system they serve by piping not exceeding 1 ¼ inch in diameter, or that have a volume of 3 cubic feet (0.085 m3) or more of cation exchange media shall have a rated salt efficiency of not less than 4,000 grains of total hardness exchange per pound of salt (477 g of total hardness exchange per kg of salt), based on sodium chloride equivalency and shall be listed as compliant with NSF/ANSI 44.. All other water softeners shall have a rated salt efficiency of not less than 3,500 grains of total hardness exchange per pound of salt (477 g of total hardness exchange per kg of salt), based on sodium chloride equivalency .

704.2 Reverse osmosis water rreatment systems.  Point-of-use reverse osmosis treatment systems shall comply with NSF 58.  The discharge pipe from a reverse osmosis drinking water treatment unit shall connect to the building drainage system in accordance with Section 611.2 of the International Plumbing Code .  Point-of-use reverse osmosis systems shall be equipped with an automatic shutoff valve that prevents the production of reject water when there is no demand for treated water.

# SECTION 705

SPECIFIC WATER CONSERVATION MEASURES

705.1 Indoor ornamental fountains and water features. Where indoor ornamental fountains, indoor water features or permanent indoor irrigation systems are supplied by potable water, the building that contains them shall comply with one additional project elective from Section 710. This shall be in addition to the requirements of Table 302.1.

705.2 Metering.  Water meters shall be required for building water consumed from any source. Each potable and reclaimed source, and each onsite water system, shall be metered separately. Meters shall be installed in accordance with the requirements of the International Plumbing Code.  Each meter shall be required to be capable of communicating water consumption data remotely.

705.2.1 Metering. All potable and non-potable water supplied to the applications listed in Table 705.2.1 shall be individually metered in accordance with the requirements indicated in Table 705.2.1.  Similar appliances and equipment shall be permitted to be grouped and supplied from piping connected to a single meter.

# SECTION 706

# NON-POTABLE WATER REQUIREMENTS

# 706.1 Scope. The provisions of this section shall govern the use of non-potable water and the construction, installation, and design of systems utilizing non-potable water. The use and application of non-potable water shall comply with laws, rules and ordinances applicable in the jurisdiction.

706.2 Signage required. Where non-potable water is used for a water use application, signage shall be provided that reads as follows: “Non-potable water is utilized for [application name]. Caution: non-potable water. DO NOT DRINK.” The words shall be legibly and indelibly printed on a sign constructed of corrosion-resistant waterproof material. The letters of the words shall be not less than 0.5 inches in height and of a color in contrast to the background on which they are applied. In addition to the required wordage, the pictograph shown in Figure 706.2 shall appear on the signage required by this section. The required location of the signage and pictograph shall be in accordance with the applicable section of this code that requires the use of non-potable water.

706.3 Water quality. Non-potable water for each end use application shall meet the minimum water quality requirements as established for the application by the laws, rules and ordinances applicable in the jurisdiction.

TABLE 705.2.1

METERING REQUIREMENTS

| APPLICATION | REQUIREMENTS |
| --- | --- |
| Irrigation | Irrigation systems that are automatically controlled shall be metered. |
| Tenant Spaces | Tenant spaces that consume water shall be metered individually. |
| Onsite Water Collection Systems | The makeup water lines supplying onsite water collection systems shall be metered. |
| Ornamental Water Features | Ornamental water features with a permanently installed water supply shall be required to utilize a meter on makeup water supply lines. |
| Pools and Spas | Indoor and outdoor pools and spas shall be required to utilize a meter on makeup water supply lines. |
| Cooling Towers | Cooling towers or groups of towers shall be required to utilize a meter on makeup water and blow-down water supply lines. |
| Steam Boilers | The makeup water supply line to steam boilers having a rating of 1,000,000 BTU/h or greater shall be metered. |
| Industrial Processes | Industrial processes consuming more than 1,000 gallons per day on average shall be metered individually. |
| Evaporative Coolers | Evaporative coolers supplying in excess of 0.6 gpm, on average, makeup water shall be. |
| Fluid Coolers and Chillers | Water-cooled fluid coolers and chillers that do not utilize closed-loop recirculation shall be metered. |
| Roof Spray Systems | Roof spray systems for irrigating vegetated roofs or thermal conditioning shall be metered. |

Figure 706.2 Pictograph – DO NOT DRINK

SECTION 707

Rainwater collection and distribution systems.

707.1 Scope. The provisions of this section shall govern the construction, installation, alteration, and repair of rainwater collection and conveyance systems.

707.2 Permits.  Permits shall be required for the construction, installation, alteration, and repair of rainwater collection and conveyance systems.  Construction documents, engineering calculations, diagrams, and other such data pertaining to the rainwater collection and conveyance system shall be submitted with each application for permit.

707.3 Potable water connections.  Where a potable system is connected to a rainwater collection and conveyance system, the potable water supply shall be protected against backflow in accordance with Section 608 of the International Plumbing Code.

707.4 Non-Potable water connections.  Where non-potable water from different sources is combined in a system, the system shall comply with the most stringent of the requirements of this code that are applicable to such sources.

707.5 Installation.  Except as provided for in this section, all systems shall be installed in compliance with the provisions of the International Plumbing Code and manufacturer’s instructions.

707.6 Applications.  Untreated rainwater shall be utilized in accordance with Section 702 and local codes.  Treated rainwater shall be utilized in accordance with Section 706 or potable water provisions of the International Plumbing Code, as applicable, and as permitted by local codes.

707.7 Approved components and materials.  Piping, plumbing components, and materials used in the collection and conveyance systems shall be manufactured of material approved for the intended application and compatible with any disinfection and treatment systems used.

707.8 Insect and vermin control.  Inlets and vents to the system shall be protected to prevent the entrance of insects and vermin into storage tanks and piping systems. Screens installed on vent pipes, inlets, and overflow pipes shall have an aperture of not greater than 1/16 inch and shall be close-fitting.  Screen materials shall be compatible with contacting system components and shall not accelerate corrosion of system components.

707.9 Drainage.  Water drained from the roof washer or debris excluder shall not be drained to the sanitary sewer.  Such water shall be diverted from the storage tank and discharge in a location that will not cause erosion or damage to property.  Roof washers and debris excluders shall be provided with an automatic means of self draining between rain events, and shall not drain onto roof surfaces.

707.10 Freeze protection.  Where sustained freezing temperatures occur, provisions shall be made to keep storage tanks and the related piping from freezing.

707.11 Trenching requirements.  All water service piping, including piping containing rainwater, shall be separated from the building sewer by 5 feet (1524 m) of undisturbed or compacted earth.  Water service pipes, potable and non-potable, shall not be located in, under or above cesspools, septic tanks, septic tank drainage fields or seepage pits.  Buried rainwater collection and distribution piping shall comply with the requirements of Section 306 of the International Plumbing Code for support, trenching, bedding, backfilling, and tunneling.

Exceptions:

1. The required separation distance shall not apply where the bottom of the water service pipe within 5 feet (1524 mm) of the sewer is a minimum of 12 inches (305 mm) above 	the top of the highest point of the sewer and the pipe materials shall comply with the International Plumbing Code for such applications.

2. Water service pipe is permitted to be located in the same trench with a building sewer, provided such sewer is constructed of materials that comply with the International Plumbing Code for such installations.

3. The required separation distance shall not apply where a potable or non-potable water 	service pipe crosses a sewer pipe provided the water service pipe is sleeved to at least 5 feet (1524 mm) horizontally from the sewer pipe centerline on both sides of such crossing with pipe materials that comply with the International Plumbing Code for such applications.

4. Irrigation piping located outside of a building and downstream of the backflow preventer is not required to meet the trenching requirements where rainwater is used for outdoor applications.

707.12 Rainwater catchment and collection systems. The design of rainwater collection and conveyance systems shall conform to accepted engineering practice.

707.12.1 Collection surface.  Rainwater shall be collected only from above-ground impervious roofing surfaces constructed from approved materials. Collection of water from vehicular parking or pedestrian surfaces shall be prohibited except where the water is used exclusively for landscape irrigation. Overflow, condensate discharge and bleed-off pipes from roof-mounted appliances including but not limited to evaporative coolers, water heaters, and solar water heaters shall not discharge onto rainwater collection surfaces.

707.12.1.1 Potable water applications.   Where collected water is to be treated to potable water standards, wood or cedar shake roofing materials, roofing materials treated with biocides, and lead flashing is prohibited on collection surfaces.  Painted surfaces are acceptable only where paint has been certified to ensure that the toxicity level of the paint is acceptable for drinking water contact. Lead, chromium or zinc based paints are not permitted on rainwater collection surfaces.  Flat roofing products shall be certified to NSF P151.  Rainwater shall not be collected from vegetated roof systems.

707.12.2 Debris excluders.  Downspouts and leaders shall be connected to a roof washer and shall be equipped with a debris excluder or equivalent device to prevent the contamination of collected rainwater with leaves, sticks, pine needles and similar material.  Debris excluders and equivalent devices shall be self-cleaning.

707.12.3 Roof gutters and downspouts.  Gutters and downspouts shall be constructed of materials compatible with the rainwater quality and collection surface.  Joints shall be sealed against leakage.  Where the collected rainwater is to be used for potable applications, gutters and downspouts shall be constructed of materials approved for drinking water applications and flashing and joints shall not be made of lead.

707.12.3.1 Slope. Roof gutters, leaders, and rainwater collection piping shall slope continuously toward collection inlets and shall be free of leaks. Gutters and downspouts shall have a slope of not less than 1/8 inch per foot along their entire length, and shall not permit the collection or pooling of water at any point.

Exception.  Siphonic drainage systems installed in accordance with the manufacturer’s installation instructions shall not be required to have slope.

707.12.3.2 Size. Gutters and downspouts shall be installed and sized in accordance with Section 1106.6 of the International Plumbing Code and local rainfall rates.

707.12.3.3 Cleanouts. Cleanouts shall be provided in the water conveyance system so as to allow access to all filters, flushes, pipes and downspouts.

707.12.4 Collection pipe materials.  In buildings where rainwater collection and conveyance systems are installed, drainage piping approved for use within plumbing drainage systems shall be utilized to collect rainwater and convey it to the storage tank.  Vent piping approved for use within plumbing venting systems shall be utilized for all vents within the rainwater system.  Drains to a storm water discharge shall use approved waste piping.

707.12.4.1 Joints. Collection piping conveying rainwater shall utilize joints approved for use with the distribution piping and appropriate for the intended applications as specified in the International Plumbing Code.

707.12.4.2 Size.  Collection piping conveying rainwater from collection surfaces shall be sized in accordance with local Chapter 11 of the International Plumbing Code and local rainfall rates.

707.12.4.3 Labeling and marking.  Additional marking of rainwater collection piping shall not be required beyond that required for sanitary drainage, waste, and vent piping by the International Plumbing Code.

707.12.5 Filtration.  Collected rainwater shall be filtered to the level required for the intended end use. Filters shall be accessible for inspection and maintenance.

707.12.6 Disinfection. Where the intended application and initial quality of the collected rainwater requires disinfection or other treatment or both, the collected rainwater shall be treated as needed to ensure that the required water quality is delivered at the point of use.

707.12.7 Storage tank.  The design of the storage tank shall be in accordance with Sections 707.12.7.1 through 707.12.7.11.

707.12.7.1 Location.  Storage tanks shall be installed either above or below grade. Above grade storage tanks shall be protected from direct sunlight and shall be constructed using opaque, UV resistant materials including, but not limited to, heavily tinted plastic, lined metal, concrete, wood, or painted to prevent algae growth, or shall have specially constructed sun barriers including but not limited to installation in garages, crawlspaces, or sheds.  Storage tanks and their manholes shall not be located directly under any soil or waste piping or any source of contamination.  Rainwater storage tanks shall be located with a minimum horizontal distance between various elements as indicated in Table 707.12.7.1.

TABLE 707.12.7.1

LOCATION OF RAINWATER STORAGE TANKS

| Element | Minimum Horizontal Distance from Storage Tank (feet) |
| --- | --- |
| Lot line adjoining private lots | 5 |
| Seepage pits | 5 |
| Septic tanks | 5 |

707.12.7.2 Materials. Where water is collected onsite, it shall be collected in an approved tank constructed of durable, nonabsorbent and corrosion-resistant materials. Where collected water is to be treated to potable water standards, tanks shall not be constructed of recycled materials and shall be constructed of materials in accordance with the International Plumbing Code.  Storage tanks shall be constructed of materials compatible with the type of disinfection system used to treat water upstream of the tank and used to maintain water quality within the tank.

707.12.7.2.1 Wooden tanks. Wooden storage tanks shall be provided with a flexible tank liner.

707.12.7.3 Foundation and supports.  Storage tanks shall be supported on a firm base capable of withstanding the storage tank’s weight when filled to capacity.  Where earthquake loads are applicable in accordance with the International Building Code, above-ground collection tank supports shall be designed and installed for the seismic forces in accordance with the International Building Code.

707.12.7.3.1 Ballast.  Where the soil can become saturated, an underground storage tank shall be ballasted, or otherwise secured, to prevent the tank from floating out of the ground when empty. The combined weight of the tank and hold down ballast shall meet or exceed the buoyancy force of the tank. Where the installation requires a foundation, the foundation shall be flat and shall be designed to support the storage tank weight when full, consistent with bearing capability of adjacent soil.

707.12.7.3.2 Structural support.  When installed below grade, storage tank installations shall be designed to withstand earth and surface structural loads without damage and with minimal deformation when filled with water or empty.

707.12.7.4 Makeup water.  Where an uninterrupted supply is required for the intended application, potable or municipally supplied reclaimed or recycled water shall be provided as a source of makeup water for the storage tank. The potable or reclaimed or recycled water supply shall be protected against backflow by means of an air gap not less than 4 inches (102 mm) above the overflow or an approved backflow device in accordance with the International Plumbing Code.  There shall be a full-open valve located on the makeup water supply line to the storage tank. Inlets to storage tank shall be controlled by fill valves or other automatic supply valves installed so as to prevent the tank from overflowing and to prevent the water   from dropping below a predetermined level.

707.12.7.5 Overflow.  The storage tank shall be equipped with an overflow pipe having the same or larger area as the sum of the areas of all tank inlet pipes. The overflow pipe shall be trapped and shall be discharged in a manner consistent with storm water runoff requirements of the jurisdiction and at a sufficient distance from the tank to avoid damaging the tank foundation.  The overflow drain shall not be equipped with a shutoff valve. A minimum of one cleanout shall be provided on each overflow pipe in accordance with Section 708 of the International Plumbing Code.

707.12.7.6 Access. A minimum of one access opening shall be provided to allow inspection and cleaning of the tank interior. All access openings to storage tanks and other vessels shall have an approved locking device or shall otherwise be protected from unauthorized access.  Below grade storage tanks, located outside of the building, shall be provided with either a manhole not less than 24 inches (610 mm) square or a manhole with an inside diameter of not less than 24 inches (610 mm). Manholes shall extend not less than 4 inches above ground or shall be gasketed and bolted to prevent water infiltration. Finish grade shall be sloped away from the manhole to divert surface water from the manhole.  Each manhole cover shall have an effective locking device.  Service ports in manhole covers shall be not less than 8 inches (203 mm) in diameter and shall be a minimum of 4 inches (102 mm) above the finished grade level.  The service port shall have an effective locking cover or a brass cleanout plug.

Exception: Storage tanks having a volume of less than 800 gallons and installed below grade shall not be required to be equipped with a manhole where provided with a service port that is not less than 8 inches (203 mm) in diameter.

707.12.7.7 Venting.  Tanks shall be provided with a vent sized in accordance with the International Plumbing Code and based on the diameter of the tank influent pipe. Tank vents shall not be connected to sanitary drainage system vents.

707.12.7.8 Inlets. Storage tank inlets shall be designed to introduce water into the tank with minimum turbulence, and shall be located and designed to avoid agitating the contents of the storage tank.

707.12.7.9 Outlets. Outlets shall be located at least 4 inches (102 mm) above the bottom of the storage tanks and shall not skim water from the surface.

707.12.7.10 Drain.  A drain shall be located at the lowest point of aboveground storage tanks and shall discharge in a manner consistent with the storm water runoff requirements of the jurisdiction and at a sufficient distance from the tank to avoid damaging the tank foundation. A minimum of one cleanout shall be provided on each drain pipe in accordance with Section 708 of the International Plumbing Code.

707.12.7.11 Labeling and signage.  Each storage tank shall be labeled with its rated capacity and the location of the upstream bypass valve. Storage tanks shall bear signage that reads as follows: “CAUTION: NON-POTABLE WATER – DO NOT DRINK.”  Where an opening is provided that could allow the entry of personnel, the opening shall bear signage that reads as follows: “DANGER – CONFINED SPACE.” Markings shall be indelibly printed on a tag or sign constructed of corrosion-resistant waterproof material mounted on the tank or shall be indelibly printed on the tank.  The letters of words shall be not less than 0.5 inches in height and shall be of a color that contrasts with the background on which they are applied.

707.12.8 Valves.  Valves shall be supplied in accordance with Sections 707.12.8.1 and 707.12.8.2.

707.12.8.1 Influent diversion. A means shall be provided to divert storage tank influent to the storm drainage system to allow maintenance and repair of the storage tank system.

707.12.8.2 Backwater valve.  Backwater valves shall be installed on each overflow and tank drain pipe.  Backwater valves shall be installed so that access is provided to the working parts for service and repair.

707.12.9 Roof washer.  A sufficient amount of rainwater shall be diverted at the beginning of each rain event, and not allowed to enter the storage tank, to wash accumulated debris from the collection surface. The amount of rainfall to be diverted shall be field adjustable as necessary to minimize storage tank water contamination. The roof washer shall not rely on manually operated valves or devices, and shall operate automatically.  Diverted rainwater shall not be drained to the roof surface, and shall be discharged in a manner consistent with the storm water runoff requirements of the jurisdiction. Roof washers shall be accessible for maintenance and service.

707.12.10 Vent piping.  Storage tanks shall be provided with a vent in accordance with the requirements of Section 707.12.7.7.  Vents shall be sized in accordance with the International Plumbing Code, based on the aggregate diameter of storage tank influent pipe(s).  Vents shall be protected from contamination by means of a U-bend installed with the opening directed downward or an approved cap.  Vent outlets shall extend a minimum of 4” above grade, or as necessary to prevent surface water from entering the storage tank.  Vent openings shall be protected against the entrance of vermin and insects in accordance with the requirements of Section 707.8.

707.12.11 Pumping and control system.  Mechanical equipment including pumps, valves and filters shall be easily accessible and removable in order to perform repair, maintenance and cleaning. Where collected rainwater is to be treated to potable water standards, the pump and all other pump components shall be listed and approved for use with potable water systems. Pressurized water shall be supplied at a pressure appropriate for the application and within the range specified by the International Plumbing Code.  Where water could be supplied at an excessive pressure, a pressure-reducing valve shall be installed in accordance with the requirements of the International Plumbing Code.

707.12.11.1 Standby power.  Where required for the intended application, automatically activated standby power, capable of powering all essential treatment and pumping systems under design conditions shall be provided.

707.12.11.2 Inlet control valve alarm.  Make-up water systems shall be fitted with a warning mechanism that alerts the user to a failure of the inlet control valve to close correctly.  The alarm shall  activate before the water within the storage tank begins to discharge into the overflow system.

707.12.11.3 Water-pressure reducing valve or regulator.  Where the rainwater pressure supplied by the pumping system exceeds 80 psi (552 kPa) static, a pressure-reducing valve shall be installed to reduce the pressure in the reclaimed water distribution system piping to 80 psi (552 kPa) static or less.  Pressure-reducing valves shall be specified and installed in accordance with Section 604.8 of the International Plumbing Code.

707.12.12 Distribution pipe.  Distribution piping shall comply with Sections 707.12.12.1 through 707.12.12.4.

707.12.12.1 Materials.  Distribution piping conveying rainwater shall conform to the standards and requirements specified by the International Plumbing Code for non-potable or potable water, as applicable.

707.12.12.2 Joints.  Distribution piping conveying rainwater shall utilize joints approved for use with the distribution piping and appropriate for the intended applications as specified in the International Plumbing Code.

707.12.12.3 Size.  Distribution piping conveying rainwater water shall be sized in accordance with the International Plumbing Code for the intended application or.

707.12.12.4 Labeling and marking.  Non-potable rainwater distribution piping shall be of the color purple and shall be embossed or integrally stamped or marked with the words:  “CAUTION: NONPOTAB LE WATER – DO NOT DRINK” or shall be installed with a purple identification tape or wrap. Identification tape shall be at least 3 inches wide and have white or black lettering on purple field stating “CAUTION: NON-POTABLE WATER – DO NOT DRINK”.  Identification tape shall be installed on top of non-potable rainwater distribution pipes, fastened at least every 10 feet to each pipe length and run continuously the entire length of the pipe.  Lettering shall be readily observable within the room or space where the piping is located.

Exception: Piping located outside of the building and  downstream of the backflow preventer is not required to be purple where rainwater is used for outdoor applications.

707.13 Tests and inspections.  Tests and inspection shall be performed in accordance with Sections 707.13.1 through 707.13.10.

707.13.1 Drainage and vent tests. The testing of rainwater collection piping, overflow piping, vent piping and storage tank drains shall be conducted in accordance with Section 312 of the International Plumbing Code.

707.13.2 Drainage and vent final test.  A final test shall be applied to the rainwater collection piping, overflow piping, storage tank, and tank vent piping in accordance with Section 312.4 of the International Plumbing Code.

707.13.3 Water supply system test.  The testing of makeup water supply piping and rainwater distribution piping shall be conducted in accordance with Section 312.5 of the International Plumbing Code.

707.13.4 Inspection and testing of backflow prevention assemblies.  The testing of backflow preventers and backwater valves shall be conducted in accordance with Section 312.10 of the International Plumbing Code.

707.13.5 Inspection vermin and insect protection.   All inlets and vents to the system shall be inspected to ensure that each is protected to prevent the entrance of insects or vermin into storage tank and piping systems in accordance with Section 707.8.

707.13.6 Roof gutter inspection and test.   Roof gutters shall be inspected to verify that the installation and slope is in accordance with Section 707.12.3.  Gutters shall be tested by pouring a minimum of one gallon of water into the end of the gutter opposite the collection point.  The gutter being tested shall not leak and shall not retain standing water.

707.13.7 Roofwasher test.   Roofwashers shall be tested by introducing water into the gutters.  Proper diversion of the first quantity of water in accordance with the requirements of Section 707.12.9 shall be verified.

707.13.8 Storage tank tests.  Storage tanks shall be tested in accordance with the following:

    - Storage tanks shall be filled with water to the overflow line prior to and during inspection. All seams and joints shall be left exposed and the tank shall remain water tight without leakage for a period of 24 hours.

    - After 24 hours, supplemental water shall be introduced for a period of 15 minutes to verify proper drainage of the overflow system and verify that there are no leaks.

    - Following a successful test of the overflow, the water level in the tank shall be reduced to a level that is at 2 inches below the makeup water trigger point by using the tank drain.  The tank drain shall be observed for proper operation.  The makeup water system shall be observed for proper operation, and successful automatic shutoff of the system at the refill threshold shall be verified.  Water shall not be drained from the overflow at any time during the refill test.

707.13.9 Supply pressure test.  The static water pressure at the point of use furthest from the supply shall be verified to be within the range required for the application, in accordance with Section 707.12.11.

707.13.10 Water quality test.  The quality of the water for the intended application shall be verified at the point of use in accordance with the requirements of the jurisdiction.

707.14 Operation and maintenance manuals.  Operations and maintenance materials shall be supplied in accordance with 707.14.1 through 707.14.4.

707.14.1 Manual. A detailed operations and maintenance manual shall be supplied in hardcopy form with all rainwater collection systems.

707.14.2 Schematics. The manual shall include a detailed system schematic, the locations of all system components, and a list of all system components including manufacturer and model number.

707.14.3 Maintenance procedures.  The manual shall provide a maintenance schedule and procedures for all system components requiring periodic maintenance.  Consumable parts including filters shall be noted along with part numbers.

707.14.4 Operations procedures.  The manual shall include system startup and shutdown procedures. The manual shall include detailed operating procedures for the system.

707.15 System abandonment.  If the owner of a rainwater collection and conveyance system elects to cease use of, or fails to properly maintain such system, the system shall be abandoned and shall comply with the following:

- All system piping connecting to a utility-provided water system shall be removed or disabled.

- The rainwater distribution piping system shall be replaced with an approved potable water supply piping system. Where an existing potable pipe system is already in place, the fixtures shall be connected to the existing system.

- The storage tank shall be secured from accidental access by sealing or locking tank inlets and access points, or filling with sand or equivalent.

707.16 Potable water applications.  Where collected rainwater is to be used for potable water applications, all materials contacting the water shall comply with NSF 61.

707.16.1 Water quality testing. Collected rainwater water shall be tested. Accumulated water to be tested shall be the result of not less than two rainfall events. Testing shall be in accordance with Sections 707.16.1.1 through 707.16.1.3.

707.16.1.1 Test methods. Water quality testing shall be performed in accordance with the latest edition of Standard Methods for the Examination of Water and Wastewater published by the American Public Health Association.

707.16.1.1.1 Tests required.  Accumulated rainwater shall be tested for Escherichia coli, total coliform, heterotrophic bacteria and cryptosporidium.

707.16.1.2 Test frequency. The testing of accumulated rainwater shall be performed prior to the rainwater system being connected to potable rainwater distribution system and annually thereafter.

707.16.1.3 Test records.  Test records shall be retained for not less than two years.

SECTION 708

Graywater systems

708.1 Scope. The provisions of this section shall govern the construction, installation, alteration, and repair of graywater reuse systems.

708.2 Permits.  Permits shall be required for the construction, installation, alteration, and repair of graywater systems.  Construction documents, engineering calculations, diagrams, and other such data pertaining to the graywater system shall be submitted with each application for permit in accordance with the laws, rules and ordinances applicable in the jurisdiction.

708.3 Potable water connections.  Where a potable water system is connected to a graywater system, the potable water supply shall be protected against backflow in accordance with Section 608 of the International Plumbing Code.

708.4 Non-potable water connections. Where non-potable water from different sources is combined in a system, the system shall comply with the most stringent of the requirements of this code that are applicable to such sources.

708.5 Installation.  Except as provided for in this section, all systems shall be installed in compliance with the provisions of the International Plumbing Code and manufacturer’s instructions, as applicable.

708.6 Applications.  Untreated graywater shall be utilized in accordance with Section 702 and local codes.  Treated graywater shall be utilized in accordance with Section 706 and as permitted by local codes.

708.7 Approved components and materials.  The piping, plumbing components, and materials used in graywater systems shall be manufactured of material approved for the intended application and compatible with any disinfection and treatment systems used.

708.8 Insect and vermin control.  The inlets and vents to the system shall be protected to prevent insects and vermin from entering storage tanks and piping systems. Screens installed on vent pipes and overflow pipes shall have an aperture not greater than 1/16 inch and shall be close-fitting.  Screen materials shall be compatible with contacting system components and shall not accelerate corrosion of system components

708.9 Freeze protection.  Where sustained freezing temperatures occur, provisions shall be made to keep storage tanks and the related piping from freezing.

708.10 Trenching requirements.  Water service piping, including piping containing graywater, shall be separated from the building sewer by 5 feet (1524 m) of undisturbed or compacted earth.  Graywater piping shall be separated from potable water piping underground by 5 feet (1524 m) of undisturbed or compacted earth.  Non-potable water service pipes shall not be located in, under or above cesspools, septic tanks, septic tank drainage fields or seepage pits.  Buried graywater piping shall comply with the requirements of Section 306 of the International Plumbing Code for support, trenching, bedding, backfilling, and tunneling.

Exceptions:

1. The required separation distance shall not apply where the bottom of the graywater service pipe within 5 feet (1524 mm) of the sewer is a minimum of 12 inches (305 mm) above the top of the highest point of the sewer and the pipe materials comply with the requirements of the International Plumbing Code for such applications.

2. The required separation distance shall not apply where the bottom of the potable water service pipe within 5 feet (1524 mm) of the graywater pipe is a minimum of 12 inches (305 mm) above the top of the highest point of the graywater pipe and the pipe materials comply with the requirements of the International Plumbing Code for such applications.

3. Water service pipe is permitted to be located in the same trench with a building sewer, provided that such sewer is constructed of materials that comply with the requirements of the International Plumbing Code for such applications.

4. The required separation distance shall not apply where a potable or non-potable water service pipe crosses a sewer pipe provided that the water service pipe is sleeved to at least 5 feet (1524 mm) horizontally from the sewer pipe centerline on both sides of such crossing with pipe materials that comply with the requirements of the International Plumbing Code for such applications.

5. The required separation distance shall not apply where a potable water service pipe crosses a graywater pipe provided that the potable water service pipe is sleeved for a distance of at least 5 feet (1524 mm) horizontally from the centerline of the graywater pipe on both sides of such crossing with pipe materials that comply with the requirements of the International Plumbing Code for such applications.

6.  Irrigation piping located outside of a building and downstream of the backflow preventer is not required to meet the trenching requirements where graywater is used for outdoor applications.

708.11 System abandonment.  If the owner of a graywater system elects to cease use of, or fails to properly maintain such system, the system shall be abandoned and shall comply with the following:

1. All system piping connecting to a utility-provided water system shall be removed or disabled.

2. The graywater distribution piping system shall be replaced with an approved potable water supply piping system. Where an existing potable pipe system is already in place, the fixtures shall be connected to the existing system.

3. Storage tanks shall be secured against accidental access by sealing or locking tank inlets and access points, or filling with sand or equivalent.

708.12 Graywater systems. The design of the graywater system shall conform to accepted engineering practice.

708.12.1 Graywater sources.  Graywater reuse systems shall collect waste discharge from only the following sources: bathtubs, showers, lavatories, clothes washers, and laundry trays.  Water from other approved non-potable sources including swimming pool backwash operations, air conditioner condensate, rainwater, cooling tower blow-down water, foundation drain water, steam system condensate, fluid cooler discharge water, food steamer discharge water, combination oven discharge water, industrial process water, and fire pump test water  shall also be permitted to be collected for reuse by graywater systems, as approved by the code official and as appropriate for the intended application.

708.12.1.1 Prohibited graywater sources. Wastewater containing urine or fecal matter shall not be diverted to graywater systems and shall discharge to the sanitary drainage system of the building or premises in accordance with the International Plumbing Code.  Water from reverse osmosis system reject water, water softener discharge water, kitchen sink wastewater, dishwasher wastewater, and wastewater discharged from wet-hood scrubbers shall not be collected for reuse within a graywater system.

708.12.2 Traps.  Traps serving fixtures and devices discharging wastewater to graywater reuse systems shall have a liquid seal of not less than 2 inches (51 mm) and not more than 4 inches (102 mm).  Where a trap seal is subject to loss by evaporation, a trap seal primer valve shall be installed in accordance with the International Plumbing Code.

708.12.3 Collection pipe. Graywater reuse systems shall utilize drainage piping approved for use within plumbing drainage systems to collect and convey untreated graywater.  Vent piping approved for use within plumbing venting systems shall be utilized for vents within the graywater system.  Drains to the sanitary sewer shall use approved waste piping.

708.12.3.1 Joints. Collection piping conveying untreated graywater shall utilize joints approved for use with the distribution piping and appropriate for the intended applications as specified in the International Plumbing Code.

708.12.3.2 Size.  Collection piping conveying rainwater from collection surfaces shall be sized in accordance with storm drainage sizing requirements specified in the International Plumbing Code.

708.12.3.3 Labeling and marking.   Additional marking of untreated graywater collection piping shall not be required beyond that required for sanitary drainage, waste, and vent piping by the International Plumbing Code.

708.12.4 Filtration.  Collected graywater shall be filtered as required for the intended end use.  Filters shall be accessible for inspection and maintenance.  Filters shall utilize a pressure gage or other approved method to provide indication when a filter requires servicing or replacement.  Filters shall be installed with shutoff valves installed immediately upstream and downstream to allow for isolation during maintenance.

708.12.5 Disinfection. Where the intended application for collected graywater requires disinfection or other treatment or both, collected graywater shall be disinfected as needed to ensure that the required water quality is delivered at the point of use.  Untreated graywater shall be retained in collection reservoirs for a maximum of 24 hours in accordance with Section 708.12.6.1.

708.12.6 Storage tank.  The design of the storage tank shall be in accordance with Sections 708.12.6.1 through 708.12.6.12.

708.12.6.1 Sizing. The holding capacity of the storage tank shall be sized in accordance with the anticipated demand. Where graywater is to be used in untreated form for groundwater recharge or subsurface irrigation, the storage tank shall be sized to limit the retention time of graywater to a maximum of 24 hours.

708.12.6.2 Location.  Storage tanks shall be installed above or below grade. Above grade storage tanks shall be protected from direct sunlight and shall be constructed using opaque, UV resistant, materials such as, but not limited to, heavily tinted plastic, lined metal, concrete, wood, or painted to prevent algae growth, or shall have specially constructed sun barriers including but not limited to installation in garages, crawlspaces, or sheds.  Storage tanks and their manholes shall not be located directly under any soil or waste piping or any source of contamination.  Graywater storage tanks shall be located with a minimum horizontal distance between various elements as indicated in Table 708.12.6.2.  Storage tanks containing untreated graywater shall be located a minimum horizontal distance of 5 feet from buildings, in addition to the requirements in Table 708.12.6.2.

TABLE 708.12.6.2

LOCATION OF GRAYWATER STORAGE TANKS

| Element | Minimum Horizontal Distance from Storage Tank (feet) |
| --- | --- |
| Lot line adjoining private lots | 5 |
| Seepage pits | 5 |
| Septic tanks | 5 |
| Water wells | 50 |
| Streams and lakes | 50 |
| Water service | 5 |
| Public water main | 10 |

708.12.6.3 Materials. Where collected onsite, water shall be collected in an approved tank constructed of durable, nonabsorbent and corrosion-resistant materials. The storage tank shall be constructed of materials compatible with any disinfection systems used to treat water upstream of the tank and with any systems used to maintain water quality within the tank.

708.12.6.3.1 Wood tanks. Wooden storage tanks that are not equipped with a makeup water source shall be provided with a flexible tank liner.

708.12.6.4 Foundation and supports.  Storage tanks shall be supported on a firm base capable of withstanding the storage tank’s weight when filled to capacity.  Where earthquake loads are applicable in accordance with the International Building Code, above-ground collection reservoir supports shall be designed and installed for the seismic forces in accordance with the International Building Code.

708.12.6.4.1 Ballast.  Where the soil can become saturated, an underground storage tank shall be ballasted, or otherwise secured, to prevent the tank from floating out of the ground when empty. The combined weight of the tank and hold down ballast shall meet or exceed the buoyancy force of the tank. Where the installation requires a foundation, the foundation shall be flat and shall be designed to support the storage tank weight when full, consistent with the bearing capability of adjacent soil.

708.12.6.4.2 Structural support.  Where installed below grade, storage tank installations shall be designed to withstand earth and surface structural loads without damage and with minimal deformation when filled with water or empty.

708.12.6.5 Makeup water.  Where an uninterrupted supply is required for the intended application, potable or municipally supplied reclaimed/recycled water shall be provided as a source of makeup water for the storage tank. The potable or reclaimed/recycled water supply shall be protected against backflow by means of an air gap not less than 4 inches (102 mm) above the overflow or an approved backflow device in accordance with the International Plumbing Code.  There shall be a full-open valve located on the makeup water supply line to the storage tank. Inlets to storage tank shall be controlled by fill valves or other automatic supply valves installed so as to prevent the tank from overflowing and to prevent the water level from dropping below a predetermined point. Where makeup water is provided, the water level shall not be permitted to drop below the rainwater inlet or the intake of any attached pump.

708.12.6.6 Overflow.  The storage tank shall be equipped with an overflow pipe having the same or larger area as the sum of the areas of all reservoir inlet pipes. The overflow pipe shall be trapped and shall be indirectly connected to the sanitary drainage system.  The overflow drain shall not be equipped with a shutoff valve. A minimum of one cleanout shall be provided on each overflow pipe in accordance with Section 708 of the International Plumbing Code.

708.12.6.7 Access. A minimum of one access opening shall be provided to allow inspection and cleaning of the tank interior. Access openings shall have an approved locking device or other approved method of securing access. Below grade storage tanks, located outside of the building, shall be provided with either a manhole not less than 24 inches (610 mm) square or a manhole with an inside diameter not less than 24 inches (610 mm) and extending not less than 4 inches above ground.  Finished grade shall be sloped away from the manhole to divert surface water from the manhole.  Each manhole cover shall have an effective locking device.  Service ports in manhole covers shall be not less than 8 inches (203 mm) in diameter and shall be a minimum of 4 inches (102 mm) above the finished grade level.  The service port shall have an effective locking cover or a brass cleanout plug.

Exception: Storage tanks under 800 gallons in volume installed below grade shall not be required to be equipped with a manhole, but shall have a service port not less than 8 inches (203 mm) in diameter.

708.12.6.8 Venting.  The tank shall be provided with a vent sized in accordance with the International Plumbing Code and based on the diameter of the tank influent pipe. The reservoir vent shall not be connected to sanitary drainage system vents.

708.12.6.9 Inlets. Storage tank inlets shall be designed to introduce water into the tank with minimum turbulence, and shall be located and designed to avoid agitating the contents of the storage tank.

708.12.6.10 Outlets. Outlets shall be located at least 4 inches (102 mm) above the bottom of the storage tank, and shall not skim water from the surface.

708.12.6.11 Drain.  A drain shall be located at the lowest point of the storage tank and shall be indirectly connected to the sanitary drainage system. The total area of all drains shall not be smaller than the total area of all overflow pipes. A minimum of one cleanout shall be provided on each drain pipe  in accordance with Section 708 of the International Plumbing Code.

708.12.6.12 Labeling and signage.  Each storage tank shall be labeled with its rated capacity and the location of the upstream bypass valve. The contents of storage tanks shall be identified with the words “CAUTION: NON-POTABLE WATER – DO NOT DRINK”  Where an opening is provided that could allow the entry of personnel, the opening shall be marked with the words, “DANGER – CONFINED SPACE.” Markings shall be indelibly printed on a tag or sign constructed of corrosion-resistant waterproof material mounted on the tank or shall be indelibly printed on the tank.  The letters of the words shall be not less than 0.5 inches in height and shall be of a color in contrast with the background on which they are applied.

708.12.7 Valves.  Valves shall be supplied in accordance with Sections 708.12.7.1 and 708.12.7.2.

708.12.7.1 Bypass valve.  One three-way diverter valve certified to NSF 50 or other approved device shall be installed on graywater collection piping upstream of each storage tank, or drainfield, as applicable, to divert untreated graywater sources to the sanitary sewer to allow servicing and inspection of the system.  Bypass valves shall be installed downstream of fixture traps and vent connections Bypass valves shall be labeled to indicate the direction of flow, connection and storage tank or drainfield connection. Bypass valves shall be installed in accessible locations. Two shutoff valves shall not be installed to serve as a bypass valve.

708.12.7.2 Backwater valve.  Backwater valves shall be installed on each overflow and tank drain pipe.  Backwater valves shall be installed so that access is provided to the working parts for service and repair.

708.12.8 Vent piping.  Storage tanks shall be provided with a vent in accordance with the requirements of Section 708.12.6.8.  Vents shall be sized in accordance with the International Plumbing Code, based on the aggregate diameter of storage tank influent pipes.  Open vents shall be protected from contamination by means of a U-bend installed with the opening directed downward or an approved cap.  Vent outlets shall extend a minimum of 4 inches above grade, or as necessary to prevent surface water from entering the storage tank.  Vent openings shall be protected against the entrance of vermin and insects in accordance with the requirements of Section 708.8.

708.12.9 Pumping and control system.  Mechanical equipment including pumps, valves and filters shall be accessible and removable in order to perform repair, maintenance and cleaning. Pressurized water shall be supplied at a pressure appropriate for the application and within the range specified by the International Plumbing Code.  Where water could be supplied at an excessive pressure, a pressure-reducing valve shall be installed in accordance with the requirements of the International Plumbing Code.

708.12.9.1 Standby power.  Where required for the intended application, automatically activated standby power, capable of powering all essential treatment and pumping systems under design conditions shall be provided.

708.12.9.2 Inlet control valve alarm.  Make-up water systems shall be provided with a warning mechanism that alerts the user to a failure of the inlet control valve to close correctly.  The alarm shall activate before the water within the collection reservoir storage tank begins to discharge into the overflow system.

708.12.9.3 Water-pressure reducing valve or regulator.  Where the rainwater pressure supplied by the pumping system exceeds 80 psi (552 kPa) static, a pressure-reducing valve shall be installed to reduce the pressure in the reclaimed water distribution system piping to 80 psi (552 kPa) static or less.  Pressure-reducing valves shall be specified and installed in accordance with Section 604.8 of the International Plumbing Code.

708.12.10 Distribution pipe.  Distribution piping shall comply with Sections 708.12.10.1 through 708.12.10.4.

708.12.10.1 Materials.  Distribution piping conveying graywater shall conform to standards and requirements specified by the International Plumbing Code for non-potable water.

708.12.10.2 Joints.  Distribution piping conveying graywater shall utilize joints approved for use with the distribution piping and appropriate for the intended applications as specified in the International Plumbing Code.

708.12.10.3 Size.  Distribution piping conveying graywater water shall be sized in accordance with the International Plumbing Code for the intended application or applications.

708.12.10.4 Labeling and marking.  All graywater distribution piping shall be either the color purple and embossed or integrally stamped or marked “CAUTION: NONPOTABLE WATER – DO NOT DRINK” or shall be installed with a purple identification tape or wrap. Identification tape shall be at least 3 inches wide and have white or black lettering on purple field stating “CAUTION: NON-POTABLE WATER – DO NOT DRINK”.  Identification tape shall be installed on top of graywater distribution pipes, fastened at least every 10 feet to each pipe length and run continuously the entire length of the pipe. Lettering shall be readily observable within the room or space where the piping is located.

Exception: Outside of the building, purple piping is not required downstream of the backflow preventer where graywater is used for outdoor applications.

708.13 Tests and inspections.  Tests and inspections shall be performed in accordance with Sections 708.13.1 through 708.13.9.

708.13.1 Drainage and vent test.  A pressure test shall be applied to the graywater collection piping, overflow piping, storage tank, storage tank drainage piping and tank vent piping in accordance with Section 312 of the International Plumbing Code.

708.13.2 Drainage and vent final test.  A final test shall be applied to the graywater collection piping, overflow piping, storage tank, and tank vent piping in accordance with Section 312.4 of the International Plumbing Code.

708.13.3 Water supply system test.  The testing of makeup water supply piping and rainwater distribution piping shall be conducted in accordance with Section 312.5 of the International Plumbing Code.

708.13.4 Inspection and testing of backflow prevention assemblies.  The testing of backflow preventers and backwater valves shall be conducted in accordance with Section 312.10 of the International Plumbing Code.

708.13.5 Inspection vermin and insect protection.   Inlets and vents to the system shall be inspected to verify that each is protected to prevent the entrance of insects and vermin into the storage tank and piping systems in accordance with Section 708.8.

708.13.6 Storage tank tests.  Storage tanks shall be tested in accordance with all of the following:

1. Storage tanks shall be filled with water to the overflow line prior to and during inspection. All seams and joints shall be left exposed and the tank shall remain water tight without leakage for a period of 24 hours.

2. After 24 hours, supplemental water shall be introduced for a period of 15 minutes to verify proper drainage of the overflow system and verify that there are no leaks.

3. Following the successful test of the overflow, the water level in the tank shall be reduced to a point 2 inches below the makeup water trigger point using the tank drain.  The tank drain shall be observed for proper operation.  The makeup water system shall be observed to verify proper operation, and successful automatic shutoff of the system at the refill threshold.  Water shall not be drained from the overflow at any time during the refill test.

708.13.7 Supply pressure test.  The static water pressure at the point of use furthest from the supply shall be verified to be within the range required for the application, in accordance with Section 707.12.11.

708.13.8 Water quality test.  The quality of the water for the intended application shall be verified at the point of use in accordance with the requirements of the jurisdiction.

708.14 Operation and maintenance manuals.  Operations and maintenance materials shall be supplied with graywater systems in accordance with Sections 708.14.1 through 708.14.4.

708.14.1 Manual. A detailed operations and maintenance manual shall be supplied in hardcopy form with all graywater systems.

708.14.2 Schematics. The manual shall include a detailed system schematic, locations of all system components, and a list of all system components including manufacturer and model number.

708.14.3 Maintenance procedures.  The manual shall provide a maintenance schedule and procedures for all system components requiring periodic maintenance.  Consumable parts including filters shall be noted along with part numbers.

708.14.4 Operations procedures.  The manual shall include system startup and shutdown procedures. The manual shall include detailed operating procedures for the system.

SECTION 709

Reclaimed water systems

709.1 Scope. The provisions of this section shall govern the construction, installation, alteration, and repair of systems supplying non-potable reclaimed water.

709.2 Permits.  Permits shall be required for the construction, installation, alteration, and repair of reclaimed water systems.  Construction documents, engineering calculations, diagrams, and other such data pertaining to the reclaimed system shall be submitted with each application for permit.

709.3 Potable water connections.  Connections between a reclaimed water system and a potable water system shall be protected against backflow in accordance with Section 608 of the International Plumbing Code.

709.4 Installation.  Except as provided for in this section, systems shall be installed in compliance with the provisions of the International Plumbing Code and manufacturer’s instructions, as applicable.

709.5 Applications.  Reclaimed water shall be utilized in accordance with Section 706 and local codes.

709.6 Approved components and materials.  Piping, plumbing components, and material used in the reclaimed water systems shall be manufactured of material approved for the intended application.

709.7 Water-pressure reducing valve or regulator.  Where the reclaimed water pressure supplied to the building exceeds 80 psi (552 kPa) static, a pressure-reducing valve shall be installed to reduce the pressure in the reclaimed water distribution system piping to 80 psi (552 kPa) static or less.  Pressure-reducing valves shall be specified and installed in accordance with Section 604.8 of the International Plumbing Code.

709.8 Trenching requirements.  Water service piping, including piping containing reclaimed water, shall be separated from the building sewer by 5 feet (1524 m) of undisturbed or compacted earth.  Reclaimed water piping shall be separated from potable water piping underground by 5 feet (1524 m) of undisturbed or compacted earth.  Reclaimed water service pipes shall not be located in, under or above cesspools, septic tanks, septic tank drainage fields or seepage pits.  Buried reclaimed water piping shall comply with the requirements of Section 306 of the International Plumbing Code for support, trenching, bedding, backfilling, and tunneling.

Exceptions:

1. The required separation distance shall not apply where the bottom of the reclaimed water service pipe within 5 feet (1524 mm) of the sewer is a minimum of 12 inches (305 mm) above the top of the highest point of the sewer and the pipe materials comply with the requirements of the International Plumbing Code for the application.

2. The required separation distance shall not apply where the bottom of the potable water service pipe within 5 feet (1524 mm) of the reclaimed water pipe is a minimum of 12 inches (305 mm) above the top of the highest point of the reclaimed water pipe and the pipe materials comply with the requirements of the International Plumbing Code for the application.

3. Water service pipe is permitted to be located in the same trench with a building sewer, provided such sewer is constructed of materials that comply with the requirements of the International Plumbing Code for the application.

4. The required separation distance shall not apply where a potable or non-potable water service pipe crosses a sewer pipe provided the water service pipe is sleeved to at least 5 feet (1524 mm) horizontally from the sewer pipe centerline on both sides of such crossing with pipe materials that comply with the requirements of the International Plumbing Code for the application.

5. The required separation distance shall not apply where a potable water service pipe crosses a reclaimed water pipe provided the potable water service pipe is sleeved to at least 5 feet (1524 mm) horizontally from the reclaimed water pipe centerline on both sides of such crossing with pipe materials that comply with the requirements of the International Plumbing Code for the application.

709.9 Reclaimed water systems. The design of the reclaimed water systems shall conform to accepted engineering practice.

709.9.1 Distribution pipe.  Distribution piping shall comply with Sections 709.9.1.1 through 709.9.1.4.

709.9.1.1 Materials.  Distribution piping conveying reclaimed water shall conform to standards and requirements specified by the International Plumbing Code for non-potable water.

709.9.1.2 Joints.  Distribution piping conveying reclaimed water shall utilize joints approved for use with the distribution piping and appropriate for the intended applications as specified in the International Plumbing Code.

709.9.1.3 Size.  Distribution piping conveying reclaimed water shall be sized in accordance with the International Plumbing Code for the intended application.

709.9.1.4 Labeling and marking.  Reclaimed water distribution piping shall be either the color purple and embossed or integrally stamped or marked “CAUTION: NONPOTABLE WATER – DO NOT DRINK” or be installed with a purple identification tape or wrap. Identification tape shall be at least 3 inches wide and have white or black lettering on purple field stating “CAUTION: NON-POTABLE WATER – DO NOT DRINK”.  Identification tape shall be installed on top of reclaimed water distribution pipes, fastened at least every 10 feet to each pipe length and run continuously the entire length of the pipe. Lettering shall be readily observable within the room or space where the piping is located.

Exception: Outside of the building, purple piping is not required downstream of the backflow preventer where reclaimed water is used for outdoor applications.

709.10 Tests and inspections.  Tests and inspections shall be performed in accordance with Sections 709.10.1 and 709.10.2.

709.10.1 Water supply system test.  The testing of makeup water supply piping and reclaimed water distribution piping shall be conducted in accordance with Section 312.5 of the International Plumbing Code.

709.10.2 Inspection and testing of backflow prevention assemblies.  The testing of backflow preventers shall be conducted in accordance with Section 312.10 of the International Plumbing Code.

# SECTION 710

project electives

710.1 General. Section 710 contains project electives related to water conservation and efficiency. Project electives shall not be mandatory unless selected by the owner or registered design professional and indicated in the Project Elective Checklist required by Section 303.1.

710.2 Indoor water use. This section contains project electives related to indoor water use.

710.2.1 Water conservation tier project electives. Each water conservation tier above that mandated in Table 302.1 shall be recognized as an individual project elective.

710.3 On-site wastewater treatment project elective. Where projects are intended to qualify for an on-site wastewater treatment project elective in accordance with Section 303.4, all wastewater from the building shall be treated on-site to tertiary standards and reused on site.

710. 4 Non-potable outdoor water supply project elective. Where projects are intended to qualify for a non-potable outdoor water supply project elective in accordance with Section 303.4, sillcocks, hose bibs, wall hydrants, yard hydrants, and other outdoor outlets shall be supplied by non-potable water.  Such outlets shall be located in a locked vault or shall be operable only by means of a removable key.

710.4.1 Labeling and signage. Each outlet shall be provided with signage in accordance with Section 706.2.

710.5 Non-potable water for plumbing fixture flushing water project elective. Where projects are intended to qualify for a non-potable water for plumbing fixture flushing project elective in accordance with Section 303.4, non-potable water shall be used for flushing water closets and urinals.

710.5.1 Water quality. Non-potable water for water closet and urinal flushing shall meet minimum water quality requirements as established for indoor flushing applications by local codes and regulations.  Where chlorine is used for disinfection, the non-potable water shall contain not more than 4 mg/L of chloramines or free chlorine. Where ozone is used for disinfection, the non-potable water shall not contain gas bubbles having elevated levels of ozone at the point of use.

710.5.2 Filtration required. Non-potable water utilized for water closet and urinal flushing applications shall be filtered by a 100 micron or finer filter.

710.5.3 Labeling and signage. The entries to rooms having water closets or urinals that 	are supplied with non-potable water shall be provided with signage in accordance with Section 706.2.

710.6 Automatic fire sprinkler system project elective. Where projects are intended to qualify for an automatic fire sprinklers system project elective in accordance with Section 303.4, automatic fire sprinkler systems shall be supplied with non-potable water from an on-site rainwater collection system.  Such rainwater collection system shall comply with Section 707. The requirements of Sections 710.6.1 and 710.6.2 shall apply to the fire sprinkler system and the on-site rainwater collection system.

710.6.1 Emergency power. An emergency power system complying with Chapter 27of the International Building Code shall be provided for powering the pump and controls for the on-site rainwater collection system.

710.6.2 Source volume indication. The fire command center for the building shall be equipped with a device that indicates the volume of non-potable water contained in the collection reservoir. The indicator shall be approved and shall be in compliance with NFPA 72.

710.7 Non-potable water supply to fire pumps project elective. Where projects are intended to qualify for a non-potable water supply to fire pumps project elective in accordance with Section 303.4, one or more fire pumps shall be located within 200 feet of a source of reclaimed or recycled water of sufficient quality, pressure, and capacity for fire pump applications and the fire pumps shall be connected to such source of reclaimed or recycled water. The connections shall be in accordance with Section 403.3.2 of the International Building Code.

710.7.1 Labeling and signage. Fire pumps connected to a non-potable water supply shall have signage in accordance with Section 706.2 provided at the building’s fire command center and at each fire pump.

710.8 Non-potable water for industrial process makeup water project elective. Where projects are intended to qualify for a non-potable water for industrial process makeup water project elective in accordance with Section 303.4, industrial processes requiring makeup water shall utilize non-potable water except where the process requires potable water for proper functioning.

710.8.1 Labeling and signage. All rooms containing process equipment supplied with non-potable water shall be provided with signage in accordance with Section 706.2.

710.9 Efficient hot water distribution system project elective.  Where projects are intended to qualify for an efficient hot water distribution project elective in accordance with Section 303.4, the volume of water in the piping between the source of hot water and the hot water outlets of shower, sink and lavatory fixture fittings shall not exceed 64 ounces (1.89 L). The volume of water contained in fixture branch piping that connects to a hot water circulation loop or electrically heat-traced pipe shall not exceed 24 ounces (0.47 L). The volume shall be calculated in accordance with Section 710.9.1.

710.9.1 Volume calculation.  The volume of water between the source of hot water and a given outlet shall be calculated by adding the internal volume of all piping, fittings, valves, meters, and manifolds between the source and the outlet.  Piping volumes shall be calculated using Table 702.8.2.  Where water is supplied by a circulating hot water system or an electrically heat-traced pipe, the hot water source shall be considered to be the loop or the heat -traced pipe, and the volume shall include the fitting on the loop that supplies the fixture branch.

710.10 Non-potable water for cooling tower makeup water project elective. Where projects are intended to qualify for a non-potable water for cooling tower makeup water project elective in accordance with Section 303.4, non-potable water shall be utilized for cooling tower makeup water in accordance with the requirements of Section 706.3.

710.11 Graywater collection project elective.  Where projects are intended to qualify for a graywater collection project elective in accordance with Section 303.4, wastewater from lavatories, showers, bathtubs, clotheswashers, and laundry trays shall be collected for reuse onsite in accordance with Section 708.

Chapter 8

indoor environmental quality and comfort

# SECTION 801

GENERAL

801.1 Scope and intent. The provisions of this chapter are intended to reduce the quantity of building indoor air contaminants and other pollutants that are odorous, irritating, or harmful to, and to provide an interior environment that is conducive to the health and well-being of, building occupants, neighbors and construction personnel.

801.2 Indoor air quality management plan required. An indoor air quality management plan shall be developed. Such plan shall address the methods and procedures to be used during design and construction to assure compliance with Sections 802 and 805.

# SECTION 802

BUILDING CONSTRUCTION FEATURES, OPERATIONS AND MAINTENANCE FACILITATION

802.1 Scope.  To facilitate the operation and maintenance of the completed building, the building and it systems shall comply with the requirements of Sections 802.2 though 802.5.

802.2 Air handling system access. The arrangement and location of air handling system components including, but not limited to, ducts, air handler units, fans, coils and condensate pans shall allow access for cleaning and repair of the air handling surfaces of such components. Access ports shall be installed in the air handling system to permit such cleaning and repairs. Piping, conduits, and other building components shall not be located so as to obstruct the required access ports.

802.3 Durability and cleanability of air handling surfaces. Surfaces exposed to airflow within air handling systems shall be constructed of metal except where made of nonporous materials that are resistant to deterioration that could cause release of particles into the air stream. Surfaces exposed to airflow shall not have cracks or crevices where dust can accumulate and shall be easily cleaned.

802.4 Air handling system filters. Filter racks shall be designed to prevent airflow from bypassing filters. Access doors and panels provided for filter replacement shall be fitted with flexible seals to provide an effective seal between the doors and panels and the mating filter rack surfaces. Special tools shall not be required for opening access doors and panels. Filter access panels and doors shall not be obstructed.

802.5 Insulation materials above suspended ceilings and in air plenums. Fibrous insulating materials with exposed friable fibers shall not be installed above suspended ceilings, on top of suspended ceiling panels or in air plenums.

# SECTION 803

hvac systems

803.1 Construction phase requirements. The ventilation of buildings during the construction phase shall be in accordance with sections 803.1.1 through 803.1.3.

803.1.1 Duct openings. Duct and other related air distribution component openings shall be covered with tape, plastic, sheet metal or shall be closed by an approved method to reduce the amount of dust and debris that collects in the system from the time of rough-in installation and until startup of the heating and cooling equipment. Dust and debris shall be cleaned from duct openings prior to system flush out and building occupancy.

803.1.2 Indoor air quality during construction. Temporary ventilation during construction shall be provided in accordance with Sections 803.1.2.1 through 803.1.2.3.

803.1.2.1 Ventilation. Ventilation during construction shall be achieved through openings in the building envelope using natural ventilation in accordance with the provisions of the International Building Code or the International Mechanical Code, or fans that produce a minimum of three air changes per hour.

803.1.2.2 Protection of HVAC system openings. HVAC supply and return duct and equipment openings shall be protected during dust-producing operations.

803.1.2.3 Return air filters. Where a forced air HVAC system is used during construction, new return air filters shall be installed prior to system flush out and building occupancy.

803.1.3 Construction phase ductless system or filter. Where spaces are conditioned during the construction phase, space conditioning systems shall be of the ductless variety, or filters for ducted systems shall be rated at MERV 13 or higher and system equipment shall be designed to be compatible. Duct system design shall account for pressure drop across the filter.

803.2 Temperature and humidity. The temperature and humidity in occupied spaces shall comply with ASHRAE 55.

803.3 Environmental tobacco smoke control. Where the jurisdiction permits tobacco smoking by the occupants within buildings or tenant spaces, the building spaces and HVAC systems shall be designed in accordance with all of the following:

1. Spaces in which smoking is permitted shall be completely separated from all other spaces by enclosing walls, floors and ceilings constructed to resist the passage of smoke.

2. Spaces in which smoking is permitted shall be served by HVAC systems that are independent of HVAC systems that serve other spaces.

3. Egress doors in spaces in which smoking is permitted shall be self-closing.

4. Spaces in which smoking is permitted shall be ventilated as required for smoking lounges in accordance with Table 403.3 of the International Mechanical Code and shall be maintained at a negative pressure with respect to adjacent spaces of not less than 7 pa.

803.4 Isolation of pollutant sources. The isolation of pollutant sources related to print, copy and janitorial rooms, garages, hangars and vented hoods shall be in accordance with Section 808.4.1.

803.4.1 Print, copy and janitorial rooms and garages. Enclosed rooms or spaces that are greater than 200 square feet in area and that are used as a print or copy facility, janitorial room, repair garage or aircraft hangar where the use of chemicals occurs shall comply with all of the following:

1. 	The enclosing walls shall extend from the floor surface to the under side of the floor or roof deck above and shall be constructed to resist the passage of airborne chemical pollutants.

2.  	Doors in the enclosing walls shall be automatic or self-closing.

3.  	An HVAC system shall be provided that: provides separate exhaust airflow to the outdoors at a rate of not less than 0.50 cfm per square foot; that maintains a negative pressure of not less than 7pa within the room; and that prohibits the recirculation of air from the room to other portions of the building.

803.5 Ductless system and filters. Filters for ducted space conditioning systems shall be rated at MERV 6 or higher and system equipment shall be designed to be compatible. The duct system design shall account for pressure drop across the filter.

# SECTION 804

SPECIFIC indoor air quality & Pollutant Control MEASURES

804.1 Fireplaces and appliances. Where located within buildings, fireplaces, solid fuel-burning appliances, gas fireplaces, gas fireplace heaters and decorative appliances for installation in fireplaces shall comply with Sections 804.1.1 through 804.1.7. Unvented room heaters shall be prohibited.

804.1.1 Installation.  Fireplaces and appliances shall be installed in accordance with the manufacturer’s instructions.

804.1.2 Venting. Fireplaces and fuel-burning appliances shall be vented to the outdoors, and shall be provided with combustion air in accordance with the International Mechanical Code and the International Fuel Gas Code.

804.1.3 Gas fireplaces. Gas fireplaces and gas fireplace heaters shall be equipped with permanently fixed glass fronts or gasketed doors and shall be listed in accordance with CSA Z21.50/CSA 2.22 and CSA Z21.88a/CSA 2.33a, respectively.

804.1.4 Fireplaces. Wood-burning fireplaces shall be provided with combustion air directly from the outdoors and shall be provided with a means to tightly close off the chimney flue and combustion air outlets when the fireplace is not in use.

804.1.5 Wood- fired appliances. Wood stoves and wood fireplace inserts shall be listed in accordance with UL 1482 and shall be certified in accordance with the requirements of the EPA Standards of Performance for New Residential Wood Heaters, 40 CFR Part 60 subpart AAA.

804.1.6 Biomass appliances. Biomass stoves and inserts shall be listed in accordance with ASTM E1509. Biomass boilers and furnaces shall be listed in accordance with CSA B366.1-2009.

804.1.7 Masonry heaters. Masonry Heaters shall be listed in accordance ASTM E1602 and shall comply with Section 2112.1 of the International Building Code.

804.2 Radon mitigation. Buildings in High Radon Potential (Zone 1) locations, as determined by Figure 804.2(1) and Table 804.2 shall comply with Sections 804.2.1 through 804.2.10.

FIGURE 804.2

EPA MAP OF RADON ZONES

a. pCi/L standard for picocuries per liter of radon gas. EPA recommends that all homes that measure 4 pCi/L and greater be mitigated

The United States Environmental Protection Agency and the United States Geological Survey have evaluated the radon potential in the United States and have developed a map of radon zones designed to assist code  officials in deciding whether radon-resistant features are applicable in new construction.

The map assigns each of the 3,141 counties in the United States to one of three zones based on radon potential. Each zone designation reflects the average short-term radon measurement that can be expected to be measured in a building without the implementation of radon control methods. The radon zone designation of highest priority is Zone 1. Table 804.2 lists the Zone 1 counties illustrated on the map. More detailed information can be obtained from state-specific booklets (EPA-402-R-93-021 through 070) available through State Radon Offices or from U.S. EPA Regional Offices.

| ALABAMA ALABAMA ALABAMA Calhoun Clay Cleburne Colbert Coosa Franklin Jackson Lauderdale Lawrence Limestone Madison Morgan Talladega CALIFORNIA Santa Barbara Ventura COLORADO Adams Arapahoe Baca Bent Boulder Chaffee Cheyenne Clear Creek Crowley Custer Delta Denver Dolores Douglas El Paso Elbert Fremont Garfield Gilpin Grand Gunnison Huerfano Jackson Jefferson Kiowa Kit Carson Lake Larimer Las Animas Lincoln Logan Mesa Moffat Montezuma Montrose Morgan Otero Ouray Park Phillips Pitkin Prowers Pueblo Rio Blanco San Miguel Summit Teller Washington Weld Yuma | CONNECTICUT Fairfield Middlesex New Haven New London GEORGIA Cobb De Kalb Fulton Gwinnett IDAHO Benewah Blaine Boise Bonner Boundary Butte Camas Clark Clearwater Custer Elmore Fremont Gooding Idaho Kootenai Latah Lemhi Shoshone Valley ILLINOIS Adams Boone Brown Bueau Calhoun Carroll Cass Champaign Coles De Kalb De Witt Douglas Edgar Ford Fulton Greene Grundy Hancock Henderson Henry Iroquois Jersey Jo Daviess Kane Kendall Knox La Salle Lee Livingston Logan Macon Marshall Mason McDonough McLean Menard Mercer | Morgan Moultrie Ogle Peoria Piatt Pike Putnam Rock Island Sangamon Schuyler Scott Stark Stephenson Tazewell Vermilion Warren Whiteside Winnebago Woodford INDIANA Adams Allen Bartholomew Benton Blackford Boone Carroll Cass Clark Clinton De Kalb Decatur Delaware Elkhart Fayette Fountain Fulton Grant Hamilton Hancock Harrison Hendricks Henry Howard Huntington Jay Jennings Johnson Kosciusko Lagrange Lawrence Madison Marion Marshall Miami Monroe Montgomery Noble Orange Putnam Randolph Rush Scott Shelby Steuben St. Joseph Tippecanoe Tipton Union Vermillion | Wabash Warren Washington Wayne Wells White Whitley IOWA All Counties KANSAS Atchison Barton Brown Cheyenne Clay Cloud Decatur Dickinson Douglas Ellis Ellsworth Finney Ford Geary Gove Graham Grant Gray Greeley Hamilton Haskell Hodgeman Jackson Jewell Johnson Keary Kingman Kiowa Lane Leavenworth Lincoln Logan Marion Marshall McPherson Meade Mitchell Nemaha Ness Norton Osborne Ottawa Pawnee Phillips Pottawatomie Pratt Rawlins Republic Rice Riley Rooks Rush Russell Saline Scott Sheridan Sherman Smith Stanton | Thomas Trego Wallace Washington Wichita Wyandotte KENTUCKY Adair Allen Barren Bourbon Boyle Bullitt Casey Clark Cumberland Fayette Franklin Green Harrison Hart Jefferson Jessamine Lincoln Marion Mercer Metcalfe Monroe Nelson Pendleton Pulaski Robertson Russell Scott Taylor Warren Woodford MAINE Androscoggin Aroostook Cumberland Franklin Hancock Kennebec Lincoln Oxford Penobscot Piscataquis Somerset York MARYLAND Baltimore Calvert Carroll Frederick Harford Howard Montgomery Washington MASS. Essex Middlesex Worcester MICHIGAN Branch Calhoun | Cass Hillsdale Jackson Kalamazoo Lenawee St. Joseph Washtenaw MINNESOTA Becker Big Stone Blue Earth Brown Carver Chippewa Clay Cottonwood Dakota Dodge Douglas Faribault Fillmore Freeborn Goodhue Grant Hennepin Houston Hubbard Jackson Kanabec Kandiyohi Kittson Lac Qui Parle Le Sueur Lincoln Lyon Mahnomen Marshall Martin McLeod Meeker Mower Murray Nicollet Nobles Norman Olmsted Otter Tail Pennington Pipestone Polk Pope Ramsey Red Lake Redwood Renville Rice Rock Roseau Scott Sherburne Sibley Stearns Steele Stevens Swift Todd Traverse Wabasha Wadena Waseca | Washington Watonwan Wilkin Winona Wright Yellow Medicine MISSOURI Andrew Atchison Buchanan Cass Clay Clinton Holt Iron Jackson Nodaway Platte MONTANA Beaverhead Big Horn Blaine Broadwater Carbon Carter Cascade Chouteau Custer Daniels Dawson Deer Lodge Fallon Fergus Flathead Gallatin Garfield Glacier Granite Hill Jefferson Judith Basin Lake Lewis and Clark Liberty Lincoln Madison McCone Meagher Mineral Missoula Park Phillips Pondera Powder River Powell Prairie Ravalli Richland Roosevelt Rosebud Sanders Sheridan Silver Bow Stillwater Teton Toole Valley Wibaux |
| --- | --- | --- | --- | --- | --- | --- |

(continued)

TABLE 804.2 – continued

HIGH RADON POTENTIAL (ZONE 1) COUNTIESa

| Yellowstone National Park NEBRASKA Adams Boone Boyd Burt Butler Cass Cedar Clay Colfax Cuming Dakota Dixon Dodge Douglas Fillmore Franklin Frontier Furnas Gage Gosper Greeley Hamilton Harlan Hayes Hitchcock Hurston Jefferson Johnson Kearney Knox Lancaster Madison Nance Nemaha Nuckolls Otoe Pawnee Phelps Pierce Platte Polk Red Willow Richardson Saline Sarpy Saunders Seward Stanton Thayer Washington Wayne Webster York NEVADA Carson City Douglas Eureka Lander Lincoln Lyon Mineral Pershing White Pine NEW HAMPSHIRE Carroll | NEW JERSEY Hunterdon Mercer Monmouth Morris Somerset Sussex Warren NEW MEXICO Bernalillo Colfax Mora Rio Arriba San Miguel Santa Fe Taos NEW YORK Albany Allegany Broome Cattaraugus Cayuga Chautauqua Chemung Chenango Columbia Cortland Delaware Dutchess Erie Genesee Greene Livingston Madison Onondaga Ontario Orange Otsego Putnam Rensselaer Schoharie Schuyler Seneca Steuben Sullivan Tioga Tompkins Ulster Washington Wyoming Yates N. CAROLINA Alleghany Buncombe Cherokee Henderson Mitchell Rockingham Transylvania Watauga N. DAKOTA All Counties OHIO Adams Allen Ashland | Auglaize Belmont Butler Carroll Champaign Clark Clinton Columbiana Coshocton Crawford Darke Delaware Fairfield Fayette Franklin Greene Guernsey Hamilton Hancock Hardin Harrison Holmes Huron Jefferson Knox Licking Logan Madison Marion Mercer Miami Montgomery Morrow Muskingum Perry Pickaway Pike Preble Richland Ross Seneca Shelby Stark Summit Tuscarawas Union Van Wert Warren Wayne Wyandot PENNSYLVANIA Adams Allegheny Armstrong Beaver Bedford Berks Blair Bradford Bucks Butler Cameron Carbon Centre Chester Clarion Clearfield Clinton Columbia Cumberland Dauphin | Delaware Franklin Fulton Huntingdon Indiana Juniata Lackawanna Lancaster Lebanon Lehigh Luzerne Lycoming Mifflin Monroe Montgomery Montour Northampton Northumberland Perry Schuylkill Snyder Sullivan Susquehanna Tioga Union Venango Westmoreland Wyoming York RHODE ISLAND Kent Washington S. CAROLINA Greenville S. DAKOTA Aurora Beadle Bon Homme Brookings Brown Brule Buffalo Campbell Charles Mix Clark Clay Codington Corson Davison Day Deuel Douglas Edmunds Faulk Grant Hamlin Hand Hanson Hughes Hutchinson Hyde Jerauld Kingsbury Lake Lincoln Lyman Marshall McCook McPherson | Miner Minnehaha Moody Perkins Potter Roberts Sanborn Spink Stanley Sully Turner Union Walworth Yankton TENNESEE Anderson Bedford Blount Bradley Claiborne Davidson Giles Grainger Greene Hamblen Hancock Hawkins Hickman Humphreys Jackson Jefferson Knox Lawrence Lewis Lincoln Loudon Marshall Maury McMinn Meigs Monroe Moore Perry Roane Rutherford Smith Sullivan Trousdale Union Washington Wayne Williamson Wilson UTAH Carbon Duchesne Grand Piute Sanpete Sevier Uintah VIRGINIA Alleghany Amelia Appomattox Augusta Bath Bland Botetourt | Bristol Brunswick Buckingham Buena Vista Campbell Chesterfield Clarke Clifton Forge Covington Craig Cumberland Danville Dinwiddie Fairfax Falls Church Fluvanna Frederick Fredericksburg Giles Goochland Harrisonburg Henry Highland Lee Lexington Louisa Martinsville Montgomery Nottoway Orange Page Patrick Pittsylvania Powhatan Pulaski Radford Roanoke Rockbridge Rockingham Russell Salem Scott Shenandoah Smyth Spotsylvania Stafford Staunton Tazewell Warren Washington Waynesboro Winchester Wythe WASHINGTON Clark Ferry Okanogan Pend Oreille Skamania Spokane Stevens W. VIRGINIA Berkeley Brooke Grant Greenbrier Hampshire Hancock Hardy Jefferson | Marshall Mercer Mineral Monongalia Monroe Morgan Ohio Pendleton Pocahontas Preston Summers Wetzel WISCONSIN Buffalo Crawford Dane Dodge Door Fond du Lac Grant Green Green Lake Iowa Jefferson Lafayette Langlade Marathon Menominee Pepin Pierce Portage Richland Rock Shawano St. Croix Vernon Walworth Washington Waukesha Waupaca Wood WYOMING Albany Big Horn Campbell Carbon Converse Crook Fremont Goshen Hot Springs Johnson Laramie Lincoln Natrona Niobrara Park Sheridan Sublette Sweetwater Teton Uinta Washakie |
| --- | --- | --- | --- | --- | --- | --- |

a. EPA recommends that the county testing be supplemented with other available State and local data to further understand the radon potential of Zone 1 areas.

804.2.1 Subfloor preparation. A layer of gas-permeable material shall be placed under all concrete slabs and other floor systems that directly contact the ground and are within the walls of the occupied spaces of the building, to facilitate future installation of a sub-slab depressurization system, if needed. The gas-permeable layer shall consist of one of the following:

1. A uniform layer of clean aggregate, a minimum of 4 inches (102 mm) thick. The aggregate shall consist of material that will pass through a 2-inch (51 mm) sieve and be retained by a 1/4-inch (6.4 mm) sieve.

2. A uniform layer of sand (native or fill), a minimum of 4 inches (102 mm) thick, overlain by a layer or strips of geotextile drainage matting designed to allow the lateral flow of soil gases.

3. Other materials, systems or floor designs with demonstrated capability to permit depressurization across the entire sub-floor area.

804.2.2 Soil-gas-retarder. A minimum 6-mil (0.15 mm) [or 3-mil (0.075 mm) cross-laminated] polyethylene or equivalent flexible sheeting material shall be placed on top of the gas-permeable layer prior to casting the slab or placing the floor assembly to serve as a soil-gas-retarder by bridging any cracks that develop in the slab or floor assembly and to prevent concrete from entering the void spaces in the aggregate base material. The sheeting shall cover the entire floor area with separate sections of sheeting lapped at least 12 inches (305 mm). The sheeting shall fit closely around any pipe, wire or other penetrations of the material. All punctures or tears in the material shall be sealed or covered with additional sheeting.

804.2.3 Entry routes. Potential radon entry routes shall be closed in accordance with Sections 804.2.3.1 through 804.2.3.10.

804.2.3.1 Floor openings. Openings around bathtubs, showers, water closets, pipes, wires or other objects that penetrate concrete slabs or other floor assemblies shall be filled with a polyurethane caulk or equivalent sealant applied in accordance with the manufacturer's recommendations.

804.2.3.2 Concrete joints. All control joints, isolation joints, construction joints and any other joints in concrete slabs or between slabs and foundation walls shall be sealed with a caulk or sealant. Gaps and joints shall be cleared of loose material and filled with polyurethane caulk or other elastomeric sealant applied in accordance with the manufacturer's recommendations.

804.2.3.3 Condensate drains. Condensate drains shall be trapped or routed through nonperforated pipe to daylight.

804.2.3.4 Sumps. Sump pits open to soil or serving as the termination point for sub-slab or exterior drain tile loops shall be covered with a gasketed or otherwise sealed lid. Sumps used as the suction point in a sub-slab depressurization system shall have a lid designed to accommodate the vent pipe. Sumps used as a floor drain shall have a lid equipped with a trapped inlet.

804.2.3.5 Foundation walls. Hollow block masonry foundation walls shall be constructed with either a continuous course of solid masonry, one course of masonry grouted solid, or a solid concrete beam at or above finished ground surface to prevent passage of air from the interior of the wall into the living space. Where a brick veneer or other masonry ledge is installed, the course immediately below that ledge shall be sealed. Joints, cracks or other openings around all penetrations of both exterior and interior surfaces of masonry block or wood foundation walls below the ground surface shall be filled with polyurethane caulk or equivalent sealant. Penetrations of concrete walls shall be filled.

804.2.3.6 Dampproofing. The exterior surfaces of portions of concrete and masonry block walls below the ground surface shall be dampproofed.

804.2.3.7 Air-handling units. Air-handling units in crawl spaces shall be sealed to prevent air from being drawn into the unit. 

Exception: Units with gasketed seams or units that are otherwise sealed by the manufacturer to prevent leakage.

804.2.3.8 Ducts. Ductwork passing through or beneath a slab shall be of seamless material unless the air-handling system is designed to maintain continuous positive pressure within such ducting. Joints in such ductwork shall be sealed to prevent air leakage.

804.2.3.9 Crawl space floors. Openings around all penetrations through floors above crawl spaces shall be caulked or otherwise filled to prevent air leakage.

804.2.3.10 Crawl space access. Access doors and other openings or penetrations between basements and adjoining crawl spaces shall be closed, gasketed or otherwise filled to prevent air leakage.

804.2.4 Passive submembrane depressurization system. In buildings with crawl space foundations, the following components of a passive sub-membrane depressurization system shall be installed during construction. 

Exception: Buildings in which an approved mechanical crawl space ventilation system or other equivalent system is installed.

804.2.4.1 Ventilation. Crawl spaces shall be provided with vents to the exterior of the building.

804.2.4.2 Soil-gas-retarder. The soil in crawl spaces shall be covered with a continuous layer of minimum 6-mil (0.15 mm) polyethylene soil-gas-retarder. The ground cover shall be lapped a minimum of 12 inches (305 mm) at joints and shall extend to all foundation walls enclosing the crawl space area.

804.2.4.3 Vent pipe. A plumbing tee or other approved connection shall be inserted horizontally beneath the sheeting and connected to a 3- or 4-inch-diameter (76 mm or 102 mm) fitting with a vertical vent pipe installed through the sheeting. The vent pipe shall be extended up through the building floors, terminate at least 12 inches (305 mm) above the roof in a location at least 10 feet (3048 mm) away from any window or other opening into the conditioned spaces of the building that is less than 2 feet (610 mm) below the exhaust point, and 10 feet (3048 mm) from any window or other opening in adjoining or adjacent buildings.

804.2.5 Passive subslab depressurization system. In basement or slab-on-grade buildings, the following components of a passive sub-slab depressurization system shall be installed during construction.

804.2.5.1 Vent pipe. A minimum 3-inch-diameter (76 mm) ABS, PVC or equivalent gas-tight pipe shall be embedded vertically into the sub-slab aggregate or other permeable material before the slab is cast. A "T" fitting or equivalent method shall be used to ensure that the pipe opening remains within the sub-slab permeable material. Alternatively, the 3-inch (76 mm) pipe shall be inserted directly into an interior perimeter drain tile loop or through a sealed sump cover where the sump is exposed to the sub-slab aggregate or connected to it through a drainage system. 

The pipe shall be extended up through the building floors, terminate at least 12 inches (305 mm) above the surface of the roof in a location at least 10 feet (3048 mm) away from any window or other opening into the conditioned spaces of the building that is less than 2 feet (610 mm) below the exhaust point, and 10 feet (3048 mm) from any window or other opening in adjoining or adjacent buildings.

804.2.5.2 Multiple vent pipes. In buildings where interior footings or other barriers separate the sub-slab aggregate or other gas-permeable material, each area shall be fitted with an individual vent pipe. Vent pipes shall connect to a single vent that terminates above the roof or each individual vent pipe shall terminate separately above the roof.

804.2.6 Vent pipe drainage. All components of the radon vent pipe system shall be installed to provide positive drainage to the ground beneath the slab or soil-gas-retarder.

804.2.7 Vent pipe accessibility. Radon vent pipes shall be accessible for future fan installation through an attic or other area outside the habitable space. 

Exception: The radon vent pipe need not be accessible in an attic space where an approved roof-top electrical supply is provided for future use. 

804.2.8 Vent pipe identification. All exposed and visible interior radon vent pipes shall be identified with at least one label on each floor and in accessible attics. The label shall read: "Radon Reduction System." 

804.2.9 Combination foundations. Combination basement/crawl space or slab-on-grade/crawl space foundations shall have separate radon vent pipes installed in each type of foundation area. Each radon vent pipe shall terminate above the roof or shall be connected to a single vent that terminates above the roof. 

804.2.10 Power source. To provide for future installation of an active sub-membrane or sub-slab depressurization system, an electrical circuit terminated in an approved box shall be installed during construction in the attic or other anticipated location of vent pipe fans. An electrical supply shall also be accessible in anticipated locations of system failure alarms.

804.3 Building flush out. After construction is completed and all interior finishes are installed, the building shall be flushed-out by supplying continuous ventilation with all air handling units at their maximum outdoor air rate for at least 14 days while maintaining an internal temperature of at least 60°F, and relative humidity not higher than 60 percent. Occupancy shall be permitted to start 7 days after start of the flush-out, provided that flush-out continues for the full 14 days. The building shall not be “baked out” by increasing the temperature of the space. Where continuous ventilation is not possible, the aggregate of flush-out periods shall be equivalent to 14 days of continuous ventilation.

Exception: Group S, F, H and U occupancies shall not be required to comply with this section.

SECTION 805

ASBESTOS USE PREVENTION

805.1 Scope. The use of and  installation of asbestos in building construction shall be prevented by building design and construction control measures in accordance with Section 805.1.1.

805.1.1 Project specifications. Project specifications shall prohibit the use of and installation of asbestos-containing products in the building. The building design team shall be familiar with products in the market place that are known to or might contain asbestos.

# SECTION 806

material EMISSIONS & Pollutant Control

806.1 Interior pressed wood. Interior particleboard, hardwood plywood, and medium density fiberboard used as sub-flooring and decorative wall coverings, and in permanently installed millwork, shall be rated for exterior exposure in accordance with DOC PS 1 or DOC PS 2, made using adhesives which do not contain urea-formaldehyde (UF) resins, sealed on all sides and edges, or comply with the requirements for formaldehyde as specified in Table 806.1. Compliance shall be demonstrated following the requirements of Section 93120 of title 17, California Code of Regulations, Airborne Toxic Control Measure to Reduce Formaldehyde Emissions from Composite Wood Products.

# TABLE 806.1

FORMALDEHYDE EMISSIONS LIMITS

| PRODUCT | LIMIT (ppm) |
| --- | --- |
| Hardwood plywood | 0.05 |
| Particle board | 0.09 |
| Medium density fiberboard | 0.11 |
| Thin medium density fiberboarda | 0.13 |

a. Maximum thickness of 5/16 inch (8mm).

806.2 Adhesives and sealants. A minimum of 85 percent by weight or volume, of site applied adhesives and sealants shall comply with the VOC content limits in Table 806.2(1) or alternative VOC emissions limits in Table 806.2(2). The VOC content shall be determined in accordance with the appropriate standard being either U.S. EPA Method 24, SCAQMD Method 304, 316A or 316B. The exempt compound content shall be determined by either SCAQMD Methods 302 and 303 or ASTM D 3960. Table 806.2(1) adhesives and sealants regulatory category and VOC content compliance determination shall conform to the SCQMD Rule 1168 Adhesive and sealant Applications as amended on 1/7/05. The provisions of this section shall not apply to adhesives and sealants subject to state or federal consumer product VOC regulations.

Table 806.2(2) adhesive alternative emissions standards compliance shall be determined utilizing test methodology incorporated by reference in the CA/DHS/EHLB/R-174 Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers dated 7/15/04 including addendum 2004-1. The alternative emissions testing shall be performed by a laboratory that has the CA/DHS/EHLB/R-174 test methodology in the scope of its ISO 17025 Accreditation.

# TABLE 806.2(1)

ADHESIVE AND SEALANTS VOC LIMITS

| ADHESIVE | VOC LIMIT |
| --- | --- |
| Indoor carpet adhesives | 50 |
| Carpet pad adhesives | 50 |
| Outdoor carpet adhesives | 150 |
| Wood flooring adhesive | 100 |
| Rubber floor adhesives | 60 |
| Subfloor adhesives | 50 |
| Ceramic tile adhesives | 65 |
| VCT and asphalt tile adhesives | 50 |
| Dry wall and panel adhesives | 50 |
| Cove base adhesives | 50 |
| Multipurpose construction adhesives | 70 |
| Structural glazing adhesives | 100 |
| Single ply roof membrane adhesives | 250 |
| Architectural Sealants | 250 |
| Architectural Sealant Primer Non Porous Porous | 250 775 |
| Modified Bituminous Sealant Primer | 500 |
| Other Sealant Primers | 750 |
| CPVC solvent cement | 490 |
| PVC solvent cement | 510 |
| ABS solvent cement | 325 |
| Plastic Cement Welding | 250 |
| Adhesive Primer for Plastic | 550 |
| Contact Adhesive | 80 |
| Special Purpose Contact Adhesive | 250 |
| Structural Wood Member Adhesive | 140 |

  - VOC limit less water and less exempt compounds in grams/liter

  - For low-solid adhesives and sealants, the VOC limit is expressed in grams/liter of material as specified in Rule 1168. For all other adhesives and sealants, the VOC limits are expressed as grams of VOC per liter of adhesive or sealant less water and less exempt compounds as specified in Rule 1168.

TABLE 806.2(2)

VOC EMISSION LIMITS

| VOC | LIMIT |
| --- | --- |
| Individual | ≤ CA chronic RELa |
| Formaldehyde | ≤ 16.5 ug/m3 or ≤ 13.5 ppb |

- CA/DHS/EHLB/R-174 Chronic Reference

Exposure Level (CREL)

806.3 Architectural paints and coatings. A minimum of 85 percent by weight or volume, of site-applied interior architectural coatings shall comply with VOC content limits in Table 806.3(1) or the alternate emissions limits in Table 806.3(2). The exempt compound content shall be determined by ASTM D3960-05.

Table 806.3(2) architectural coating alternate emissions standards compliance shall be determined utilizing test methodology incorporated by reference in the CA/DHS/EHLB/R-174 Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers dated July 15, 2004 including Addendum 2004-1. The alternative emissions testing shall be performed by a laboratory that has the CA/DHS/EHLB/R-174 test methodology in the scope of its ISO 17025 Accreditation.

806.4 Flooring A minimum of 85 percent of the total area of flooring installed within the interior of the building shall comply with the requirements of Table 806.4 (2). Where flooring with more than one distinct product layer is installed, the emissions from each layer shall comply with these requirements.  The test methodology used to determine compliance shall be from CA/DHS/EHLB/R-174 Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers dated July 15, 2004 including Addendum 2004-1  The emissions testing shall be performed by a laboratory that has the CA/DHS/EHLB/R-174 test methodology in the scope of its ISO 17025 Accreditation.

Where post manufacture coatings or surface applications have not been applied, the flooring listed in Table 806.4(1) shall be deemed to comply with the requirements of Table 806.4(2).

806.5 Acoustical ceiling tiles and wall systems. A minimum of 85 percent of acoustical ceiling tiles and wall systems, by square feet, shall comply with the requirements of Table 806.5(2). Where ceiling and wall systems with more than one distinct product layer are installed, the emissions from each layer shall comply with these requirements. The test methodology used to determine compliance shall be from CA/DHS/EHLB/R-174 Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers dated July 15, 2004 including Addendum 2004-1. The emissions testing shall be performed by a laboratory that has the CA/DHS/EHLB/R-174 test methodology in the scope of its ISO 17025 Accreditation.

Where post manufacture coatings or surface applications have not been applied, the ceiling or wall systems listed in Table 806.5(1) shall be deemed to comply with the requirements of Table 806.5(2).

806.6 Insulation. A minimum of 85 percent of insulation shall comply with the requirements of Table 806.6. The test methodology used to determine compliance shall be from CA/DHS/EHLB/R-174 Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers dated July 15, 2004 including Addendum 2004-1. The emissions testing shall be performed by a laboratory that has the CA/DHS/EHLB/R-174 test methodology in the scope of its ISO 17025 Accreditation.

# TABLE 806.3(1)

VOC CONTENT LIMITS FOR ARCHITECTURAL COATINGSc,d,e

|  | Effective: JANUARY 1, 2010 | Effective: JANUARY 1, 2012 |
| --- | --- | --- |
| Coating Category | LIMITa g/l | LIMITa g/l |
| Flat Coatings | 50 |  |
| Non-flat Coatings | 100 |  |
| Non-flat - High Gloss Coatings | 150 |  |
| Specialty Coatings: |  |  |
| Aluminum Roof Coatings | 400 |  |
| Basement Specialty Coatings | 400 |  |
| Bituminous Roof Coatings | 50 |  |
| Bituminous Roof Primers | 350 |  |
| Bond Breakers | 350 |  |
| Concrete Curing Compounds | 350 |  |
| Concrete/Masonry Sealers | 100 |  |
| Driveway Sealers | 50 |  |
| Dry Fog Coatings | 150 |  |
| Faux Finishing Coatings | 350 |  |
| Fire Resistive Coatings | 350 |  |
| Floor Coatings | 100 |  |
| Form-Release Compounds | 250 |  |
| Graphic Arts Coatings (Sign Paints) | 500 |  |
| High Temperature Coatings | 420 |  |
| Industrial Maintenance Coatings | 250 |  |
| Low Solids Coatings | 120b |  |
| Magnesite Cement Coatings | 450 |  |
| Mastic Texture Coatings | 100 |  |
| Metallic Pigmented Coatings | 500 |  |
| Multi-Color Coatings | 250 |  |
| Pre-Treatment Wash Primers | 420 |  |
| Primers, Sealers, and Undercoaters | 100 |  |
| Reactive Penetrating Sealers | 350 |  |
| Recycled Coatings | 250 |  |
| Roof Coatings | 50 |  |
| Rust Preventative Coatings | 400 | 250 |
| Shellacs, Clear | 730 |  |
| Shellacs,Opaque | 550 |  |
| Specialty Primers, Sealers, and Undercoaters | 350 | 100 |
| Stains | 250 |  |
| Stone Consolidants | 450 |  |
| Swimming Pool Coatings | 340 |  |
| Traffic Marking Coatings | 100 |  |
| Tub and Tile Refinish Coatings | 420 |  |
| Waterproofing Membranes | 250 |  |
| Wood Coatings | 275 |  |
| Wood Preservatives | 350 |  |
| Zinc-Rich Primers | 340 |  |

a. Limits are expressed as VOC Regulatory (except as noted), thinned to the manufacturer’s maximum thinning recommendation, excluding any colorant added to tint bases.

b. Limit is expressed as VOC actual.

c. The specified limits remain in effect unless revised limits are listed in subsequent columns in the table.

d. Values in this table are derived from those specified by the California Air Resources Board, Architectural Coatings Suggested Control Measure, February 1, 2008.

e. Table 806.3(1) architectural coating regulatory category and VOC content compliance determination shall conform to the California Air Resources Board Suggested Control Measure for Architectural Coatings dated February 1, 2008.

# Table 806.3(2)

Architectural Coatings VOC Emission Limits

| VOC | LIMIT |
| --- | --- |
| Individual | ≤½ CA chronic RELa |
| Formaldehyde | ≤ 16.5 ug/m³ or ≤ 13.5 ppb |

a. CA Chronic Reference Exposure Level (CREL)

# TABLE 806.4 (1)

FLOORING DEEMED TO COMPLY WITH VOC EMISSION LIMITS

Ceramic tile flooring

Organic-free, mineral-based flooring

Clay brick pavers

Concrete pavers

Concrete flooring

Metal flooring

# TABLE 806.4(2)

FLOORING VOC EMISSION LIMITS

| VOC | LIMIT |
| --- | --- |
| Individual VOCs | ≤½ CA chronic RELa |
| Formaldehyde | ≤ 16.5 ug/m³ or ≤ 13.5 ppb |

a. CA Chronic Reference Exposure Level (CREL)

# TABLE 806.5 (1)

CEILING AND WALL SYSTEMS DEEMED TO COMPLY

WITH VOC EMISSION LIMITS

Ceramic tile

Organic-free, mineral-based systems

Clay brick

Concrete brick

Concrete systems

Metal systems

# TABLE 806.5(2)

ACOUSTICAL CEILING TILES AND WALL SYSTEMS

VOC EMISSION LIMITS

| VOC | LIMIT |
| --- | --- |
| Individual | ≤½ CA chronic RELa |
| Formaldehyde | ≤ 16.5 ug/m³ or ≤ 13.5 ppb |

a. CA Chronic Reference Exposure Level (CREL)

b. Defined to be the total response of measured VOCs falling

within the C6-C16 range, with responses calibrated to a

toluene surrogate.

# TABLE 806.6

INSULATION

VOC EMISSION LIMITS

| VOC | LIMIT |
| --- | --- |
| Individual VOCs | ≤½ CA chronic RELa |
| Formaldehyde | ≤ 16.5 ug/m³ or ≤ 13.5 ppb |

a. CA Chronic Reference Exposure Level (CREL)

# SECTION 807

SOUND TRANSMISSION

807.1 Sound transmission. Buildings and tenant spaces shall comply with the sound transmission requirements of Sections 807.2 through 807.5.2.

Exception.  The following buildings and spaces need not comply with this section:

1. Building or structures that have the interior environment open to the exterior environment.

2. Parking structures.

3. Concession stands and toilet facilities in Group A-4 and A-5 occupancies.

807.2 Exterior sound transmission. Where Group A1, A3, E and I occupancy buildings, Group B occupancy buildings used for educational purposes, or Group R are constructed at the locations listed in Items 1 through 4, the wall and roof-ceiling assemblies making up the building envelope shall have a sound transmission class (STC) or outdoor-indoor transmission class (OITC) of not less than 50 and the windows within the building envelope walls shall have a sound transmission class (STC) or outdoor-indoor transmission class (OITC) of not less than 30. Where the sound transmission is field tested, the sound transmission shall be not less than 45 STC or OITC for wall and roof-ceiling assemblies and not less than 25 STC or OITC for windows. Transmission classes shall be determined in accordance with ASTM E90 for sound transmission class (STC) values or ASTM E1332 for outdoor-indoor transmission class (OITC) values.

1. Within 1000 feet (300 m) of a freeway, fire station, fuel dispensing facility, factory, industrial or manufacturing zone or facilities, commercial storage facility, or sports arena or stadium.

2. Within 500 feet (150 m) of a roadway  containing  4 or more traffic lanes.

3. Within 5 miles (8 km) of a commercial airport.

4. Within 3,000 feet (900 m) of an active railway.

807.3 Interior sound transmission. Wall and floor-ceiling assemblies that separate Group A, F and M occupancies from Group B, I or R occupancies shall have a sound transmission class (STC) of not less than 50. Sound transmission classes shall be determined in accordance with ASTM E90, or for concrete masonry and clay masonry assemblies shall be calculated in accordance with TMS 0302 or determined in accordance with ASTM E90.

Exception: This section shall not apply to wall and floor-ceiling assemblies enclosing:

1. Public entrances to tenants of covered and open mall buildings.

2. Concession stands and lavatories in Group A-4 and A-5 occupancies.

807.4 Mechanical and emergency generator equipment and systems. Building mechanical and emergency generator systems shall be designed to control airborne noise in accordance with Sections 807.4.1 through 807.4.3.

807.4.1 Separating assemblies. Wall and floor-ceiling assemblies that separate a mechanical or emergency generator equipment room or space from the remainder of the building shall have a sound transmission class (STC) of not less than 60 determined in accordance with ASTM E90, or for concrete masonry and clay masonry assemblies as calculated in accordance with TMS 0302 or as determined in accordance with ASTM E90..

807.4.2 Mechanical and emergency generator equipment outside of buildings. Where mechanical equipment and emergency generators are located outside of the building envelope or are exposed to the exterior environment, an adjacent property shall not be subjected to a sound level greater than indicated in Table 807.4.2. Special inspections shall be required and conducted in accordance with Section 903.1 in order to demonstrate compliance.

807.4.3 HVAC background sound. HVAC system caused background sound levels for all modes of operation within rooms shall be in accordance with the lower and upper noise criteria (NC) limits as shown in Table 807.4.3. Special inspections shall be required and conducted in accordance with Section 903.1 in order to demonstrate compliance.

TABLE 807.4.2

MAXIMUM PERMISSIBLE A-WEIGHTED SOUND LEVELS

| Initiating Property | Adjacent Property | Maximum A-Weighted Sound Level (dB) |
| --- | --- | --- |
|  |  | Day Time | Night Time |
|  |  | 7:00 AM to 10:00 PM | 10:00 PM to 7:00 AM |
| All, except factory, industrial, or storage | All, except factory, industrial, or storage | 65 | 50 |
| Factory, industrial, or storage | All other, except factory, industrial, or storage | 65 | 50 |
| Factory, industrial, or storage | Factory, industrial, or storage | 75 | 75 |

TABLE 807.4.3

BACKGROUND SOUND IN ROOMS

| Occupancy Type | Room | Noise Criteria (NC) Limits |
| --- | --- | --- |
| Assembly-A-1 | Symphony, concert, recital halls | 25 to 30 |
|  | Music teaching studios | 25 to 30 |
|  | Music practice rooms | 30 to 35 |
|  | Motion picture theaters | 30 to 40 |
| Assembly-A-3 | Places of religious worship | 25 to 35 |
|  | Art gallery, , exhibit hall, funeral parlor, lecture halls, libraries, and museums. | 30 to 40 |
|  | Courtroom | 25 to 35 |
| Assembly-A-4 | Gymnasiums, natatoriums and seating areas | 35 to 45 |
| Business-B | Office-enclosed | 25 to 35 |
|  | Office-open plan | 35 to 45 |
|  | Corridors and lobbies | 40 to 45 |
|  | Conference rooms | 25 to 35 |
|  | Educational occupancies above 12th grade | (See Education) |
| Education - E |  |  |
|  | Core learning lecture and class rooms that are less than or equal to 20,000 cu. ft. (566 m3) in volume | 25 to 35 |
|  | Core learning lecture and class rooms that are greater than 20,000 cu. ft. (566 m3) in volume | 30 to 35 |
|  | Open plan class rooms | 25 to 35 |
|  | Administrative offices and rooms | 25 to 35 |
| Institutional-I-2 | Private rooms | 25 to 35 |
|  | Wards | 30 to 40 |
|  | Operating rooms | 25 to 35 |
|  | Corridors and public areas | 30 to 40 |
| Residentail-R-1 & R-2 | Rooms or suites | 25 to 35 |
| R-2 | Meeting rooms | 25 to 35 |
|  | Corridors and lobbies | 35 to 45 |
|  | Service areas | 35 to 45 |

807.5 Special inspections for sound transmission. An approved agency, funded by the building owner, shall furnish report(s) of test findings indicating that the results are in compliance with this section and the construction documents. Discrepancies shall be brought to the attention of the design professional and code official prior to the completion of that work. A final testing report documenting required testing and corrections of any discrepancies noted in prior tests shall be submitted at a point in time agreed upon by the building owner, or building owner’s agent, design professional, and the code official for purposes of demonstrating compliance.

807.5.1 Testing for mechanical and emergency generator equipment outside of buildings. In accordance with Section 807.4.2, all mechanical and emergency generator equipment shall be field tested in accordance with Table 903.1. Testing shall be conducted following the complete installation of the equipment or generators, the installation of sound reduction barriers, and balancing and operation of the equipment or generators. Testing shall be at locations representing the four cardinal directions from the face of the project building. Such testing shall occur on a Tuesday, Wednesday or Thursday at both the day and night times within the periods shown in Table 807.4.2.

807.5.2 Testing for HVAC background sound. Testing shall be executed in accordance with Section 807.4.3 within not less than 50 percent of the total number of rooms contained in a building or structure, exclusive of closets and storage rooms less than 50 square feet in area, and exclusive of toilet facilities in accordance with Table 903.1. Testing shall occur following the complete installation of the equipment and systems, the installation of any sound reduction barriers, and balancing and operation of the equipment and systems.

SECTION 808

DAYLIGHTING

808.1 General. The fenestration in building roofs and walls shall be placed in accordance with Sections 808.1 through 808.3.  Interior spaces shall be planned to benefit from the exposure to natural light offered by the fenestration in accordance with this section.

808.2 Applicability. Daylighting of building spaces in accordance with Section 808.3 shall be required for buildings containing Group A-3, B, E, F, M or S occupancies.

Exception.  Daylighting is not required in the following rooms and spaces:

1. A Group A3 occupancy where the specific use of the romm or space is for other than reading areas in libraries, waiting areas in transportation terminals, exhibition halls, gymnasiums and indoor athletic areas.

2. A Group B occupancy where the specific use of the room or space is for other than banks, educational facilities for students above the 12th grade, laboratories for testing and research, motor vehicle showrooms, post offices, print shops, offices and training and skill development not within a school or academic program.

3. Those portions of Group M or S occupancies located directly underneath a higher floor.

4.  Building spaces where darkness is required for the primary use of the space, including, but not limited to, light sensitive material handling and darkrooms.

5.  Building spaces that are required to be cooled below 50 degrees F.

6.  Unconditioned buildings that are equipped with exterior doors that when opened, provides equivalent daylighting as if fenestration had been provided in the building envelope.

808.3 Daylighting of building spaces.  Not less than 50 percent of the total floor area in regularly occupied spaces shall be located within a daylit area that complies with either Section 808.3.1 or Section 808.3.2.  Buildings required to have more than 25,000 square feet of daylit area shall comply with Section 808.3.2.

Exception:

Where exterior walls or roofs are fully obstructed or partially obstructed, the required daylit area shall be modified in accordance with Equation 8-1.

required daylit area  ≥ 50% x TDP	(Equation 8-1)

The total daylight potential (TDP) is a weighted average of the individual daylight potentials for each floor:

TDP	=	∑(DP1 X TF1/TF) + (DP2 X TF2/TF) + …

DP1	=	UW1/TW1 + [(1 – UW1/TW1) X (UR1/TR1)]

UW1,2,…	=	The unobstructed exterior wall area for each floor.

TW1,2,…	=	The exterior wall area for each floor.

UR1,2,…	=	The unobstructed roof area immediately above each floor.

TR1,2,…	=	The total roof area immediately above each floor.

FA1,2,…	=	The floor area of each floor.

808.3.1 Daylight prescriptive requirements.  Daylit areas shall be within a sidelighting daylight zone that complies with Section 808.4.1.1 or a toplighting daylight zone that complies with Section 808.3.1.2.

808.3.1.1  Sidelighting.  The unobstructed exterior wall adjacent to the sidelighting daylight zone shall include fenestration that complies with Table 609.5.

808.3.1.2  Toplighting.  The unobstructed roof above the toplighting daylight zone shall include fenestration that complies with Table 609.5.

808.3.2  Daylight performance requirements.  Daylight analysis conducted in accordance with Section 808.4.2.1 shall demonstrate that all points in the daylit area have a daylight saturation of not less than 60 percent.

808.3.2.2  Daylight simulation.  A climate based analysis shall comply with the following:

1. Provide data on an hourly basis for a typical meteorological year, excluding the first hour after sunrise every day and the last hour before on an hourly basis for a typical meteorological year, excluding the first hour after sunrise every day and the last hour before sunset every day.

2. Address the effects of exterior shading devices buildings, structures, and geological formations.

3. Exclude the effects of interior furniture systems, shelving, and stacks

4. Use the actual reflectance characteristics of all materials.

5. Include the effects of blinds, shades and other movable interior fenestration shading devices. The configuration of manually controlled fenestration shading devices shall be adjusted on the spring and fall equinoxes only.  The configuration of automatically controlled fenestration shading devices and fenestration with automatically controlled variable transmittance shall be adjusted to accurately represent the control system operation.

6. Calculation points shall be spaced no more than 4 feet by 4 feet.  The calculation grid shall start within 4 feet of each wall or partition.

# SECTION 809

Project electives

809.1 General. Section 809 contains project electives related to indoor air quality and environmental comfort. Project electives shall not be mandatory unless selected by the owner or registered design professional and indicated in the Project Elective Checklist required by Section 303.1.

809.2 VOC emissions project electives.  Sections 809.2.1 through 809.2.4 shall be considered to be separate project electives. The electives shall be cumulative and compliance with each project elective shall be recognized individually.

809.2.1. Flooring material project elective.  Where projects are intended to qualify for a “flooring material” project elective in accordance with Table 303.1 and Section 303.4, a minimum of 50 percent of the total area of flooring installed within the interior of the building shall be one or more of the flooring materials listed in Table 806.4(1).

809.2.2. Ceiling materials project elective. Where projects are intended to qualify for a “ceiling materials” project elective in accordance with Table 303.1 and Section 303.4, a minimum of 50 percent of ceiling systems, by square feet, shall be one or more of the ceiling systems listed in Table 806.5(1).

809.2.3. Wall materials project elective. Where projects are intended to qualify for a “wall materials” project elective in accordance with Table 303.1 and Section 303.4, a minimum of 50 percent of wall systems, by square feet, shall be one or more of the wall systems listed in Table 806.5(1).

809.2.4. Total VOC limit project elective. Where projects are intended to qualify for a “total VOC limit” project elective in accordance with Table 303.1 and Section 303.4, a minimum of 50 percent of all products addressed in Sections 806.2, 806.3, 806.4, 806.5 and 806.6 shall have a Total Volatile Organic Compounds (TVOCs) emission limit of ≤ 500 ug/m³. The test methodology used to determine compliance shall be from CA/DHS/EHLB/R-174 Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers dated July 15, 2004 including Addendum 2004-1, The emissions testing shall be performed by a laboratory that has the CA/DHS/EHLB/R-174 test methodology in the scope of its ISO 17025 Accreditation.

809.3 Views to building exterior project elective. Where projects are intended to qualify for a “views to building exterior” project elective in accordance with Table 303.1 and Section 303.4, a direct line of sight to vision glazing shall be provided for not less than 75 percent of the floor area in regularly occupied spaces that are within 40 feet of an exterior wall in the building envelope. The direct line of sight shall be measured at a height of 42 inches above the finished floor of the space.

Chapter 9

COMMISSIONING, OPERATION AND MAINTENANCE

SECTION 901

general

901.1 Scope. The provisions of this chapter are intended to facilitate the pre- and post- occupancy commissioning, operation and maintenance of buildings constructed in accordance with this code in a manner that is consistent with the intent of other provisions of this code, and to further that goal through the education of building owners and maintenance personnel with regard to related best operating and management practices.

SECTION 902

APPROVED AGENCY

902.1 Approved agency. An approved agency shall provide all of the information necessary for the code official to determine that the agency meets the applicable requirements. The code official shall be permitted to be the approved agency.

902.1.1 Independence. An approved agency shall be objective, competent and independent from the contractor responsible for the work being inspected.  The agency shall also disclose possible conflicts of interest so that objectivity can be confirmed.

902.1.2 Equipment. An approved agency shall have adequate equipment to perform the required commissioning.  The equipment shall be periodically calibrated.

902.1.3 Personnel. An approved agency shall employ experienced personnel educated in conducting, supervising and evaluating tests and commissioning.

SECTION 903

COMMISSIONING

903.1 General. Where application is made for construction as described in this section, the registered design professional in responsible charge or approved agency as identified by the registered design professional in responsible charge, shall perform commissioning during construction and after occupancy as required by Table 903.1. Where Table 903.1 specifies that commissioning is to be done on a periodic basis, the registered design professional in responsible charge shall provide a schedule of periodic commissioning with the submittal documents that shall be reviewed and approved by the code official.

The approved agency shall be qualified and shall demonstrate competence, to the satisfaction of the code official, for the commissioning of the particular type of construction or operation.  The registered design professional in responsible charge and engineers of record involved in the design of the project are permitted to act as the approved agency provided those personnel meet the qualification requirements of this section to the satisfaction of the code official.  The approved agency shall provide written documentation to the code official demonstrating competence and relevant experience or training.  Experience or training shall be considered relevant where the documented experience or training is related in complexity to the same type of commissioning activities for projects of similar complexity and material qualities.

903.1.1 Pre occupancy report requirement. The approved agency shall keep records of the commissioning required by Table 903.1. The approved agency shall furnish commissioning reports to the owner and the registered design professional in responsible charge and, upon request, to the code official.  Reports shall indicate that work was or was not completed in conformance to approved construction documents.  Discrepancies shall be brought to the immediate attention of the contractor for correction.  where discrepancies are not corrected, they shall be brought to the attention of the owner, code official and to the registered design professional in responsible charge prior to the completion of that phase of the work. Prior to the issuance of a Certificate of Occupancy, a final commissioning report shall be submitted to and accepted by the code official.

903.1.2 Post occupancy report requirement. Post occupancy commissioning shall occur as specified in the applicable sections of this code. A post occupancy commissioning report shall be provided to the owner within 30 months after the Certificate of Occupancy is issued for the project and shall be made available to the code official upon request.

TABLE 903.1

COMMISSIONING Plan

| Construction or System requiring Verification | Pre Occ. | Post Occ. | Method | Occurrence | Section/ Ref. Std. |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Pre Occ. | Post Occ. |  |
| Chapter 4: Site development and land use |
| Natural resources and base line conditions of building site | X | None | Report | With Permit Submittal | None | 402.3.1 |
| Landscape irrigation systems | X | None | Field inspection | Installation | None | 402.3.3 406.5 |
| Topsoil and Vegetation Protection Measures; Setbacks from protected areas | X | None | Field inspection and report | Installation of measures, prior to other site disturbance | None | 402.3 |
| Imported Soils | X | None | Field inspection and report | With Permit Submittal; After all fill operations complete. | None | 402.3.5.5 |
| Soil Restoration and Reuse | X | None | Field inspection and report | Preparation and replacement of soils | None | 402.3.5.4 |
| Soil Percolation Test | X | None | Field Inspection and report | Prior to installation of graywater irrigation system | None | 406.2.2 |
| Stormwater management system operation | None | X | Field Inspection |  | 24 months | 402.3.2 |
| Erosion and sediment control | X | X | Field inspection | Daily during construction activities | Periodic for 24 months | 402.3.6 |
| Hardscape and shading provided by structures and vegetation | X | X | Field inspection and report | During construction and installation | 24 months | 404.2 |
| Vegetative Roofs and Terraces | X | X | Field inspection and report | Installation of protective membranes, base materials, soils and vegetation | 24 months | 404.3.2 |
| Site Lighting | X | None | Testing and report | Installation | None | 405 |
| Chapter 5: Materials |
| Moisture Control Project Elective (Section 507.7) |  |  |  |  |  |  |
| 1. Foundation sub-soil drainage system. | X | None | Field inspection and verification | Periodic inspection for entire roof system. | None | 507.7 and IBC Ch 18 |
| 2. Foundation damp-proofing and water-proofing. | X | None | Field inspection and verification | Periodic inspection for the entire foundation. | None | 507.7 and IBC Ch 18 |
| 3. Flashing at: Windows, exterior doors, skylights, wall flashing and drainage systems. | X | None | Field inspection and verification | Periodic inspection for not less than XX% of all flashing locations. | None | 507.7 and IBC Ch 14 |
| 4. Exterior wall coverings. | X | None | Field inspection and verification | Periodic inspection for not less than 25% of exterior wall cladding systems. | None | 507.7 and IBC Ch 14 |
| 5. Roof coverings. | X | None | Field inspection and verification | Periodic inspection for the entire system. | None | 507.7 and IBC Ch 15 |
| Chapter 6 - Energy |
| Energy consumption, monitoring, targeting and reporting |  |  |  |  |  |  |
| a. Monitoring system | X | None | Inspection and verification | During construction and prior to occupancy | None | 604 |
| b. Calibration | X | X | Testing and review and evaluation or test reports | During commissioning | Annually | 604, 611 |
| Mechanical systems completion – all buildings |  |  |  |  |  |  |
| a. Air system balancing – provide the means for system balancing | X | None | Inspection and verification | During construction and prior to occupancy | None | 612.1.2.1and through reference to IECC |
| b. Hydronic system balancing – provide means for system balancing | X | None | Inspection and verification | During construction and prior to occupancy | None | 612.1.2.2 and through reference to IECC |
| c. Duct system testing | X | None | Testing, testing report and verification of results | During construction and/or at final inspection. | None | 613.5.3 and through reference to the IECC |
| d. Mechanical system manuals – construction documents to require O&M manual | X | None | Verification of construction documents | Plan review | None | 612.1.5.2 |
| Mechanical systems – buildings over 5,000 square feet total building floor area |  |  |  |  |  |  |
| a. Commissioning required and noted in plans and specifications | X | None | Verification of construction documents | Plan review | None | 612.1 |
| b. Documentation of required commissioning outcomes | X | None | Verification with the building owner | Subsequent to completion of all commissioning activities | None | 612.1 |
| c. Preparation and availability of a commissioning plan | X | None | Verification with the RDP or commissioning agent | Between plan review and commissioning initiation | None | 612.1.1 |
| d. Balance HVAC systems (both air and hydronic) | X | X | HVAC system installer/contractor or commissioning agent | After installation of HVAC systems and prior to occupancy | TBD | 612.1.2 |
| e. Functional performance testing of HVAC equipment | X | X | HVAC system installer/contractor or commissioning agent | After installation of HVAC systems and prior to occupancy | TBD | 612.1.3 |
| f. Functional performance testing of HVAC controls and control systems | X | X | HVAC system installer/contractor or commissioning agent | After installation of HVAC systems and prior to occupancy | TBD | 612.1.3.2 |
| g. Preparation of preliminary commissioning report | None | X | HVAC system installer/contractor or commissioning agent | None | Subsequent to commissioning | 612.1.4 |
| h. Acceptance of HVAC systems and equipment/system verification report | None | X | Building owner | None | Letter verifying receipt of the commissioning report | 612.1.4.1 |
| i. Preparation and distribution of final HVAC system completion - Documentation that construction documents require drawings, manuals, balancing reports and commissioning report be provided to the owner and that they have been provided | None | X | RDP, contractor or commissioning authority | None | 90 days after final certificate of occupancy | 612.1.5 |
| Ch 6 - Lighting |
| Auto demand reduction control system functionality | X | X | Functional Testing | Post Installation | 18-24 months | 605.4 |
| Plug load controls | X | None | Functional Testing | Installation | None | 609.6 |
| Connection of appliances to switched receptacles |  | X |  | Visual | None | 609.6 |
| Specified transformer nameplate efficiency rating | X | None | Visual | Installation | None | 609.8.1.1 |
| Verification of lamp | X | X | Visual | Post Installation | 18-24 months | 609.10 |
| Verification of ballast | X | None | Visual | Installation | None | 609.10 |
| Revised energy calculations to represent building as constructed | X | None | Calculations | Post Installation | None | 602 603 |
| Occupant sensor controls | X | X | Commissioning | Post Installation | 18-24 months | 609.1 |
| Automatic daylight controls | X | X | Commissioning | Post Installation | 18-24 months | 609.5 |
| Time switch controls | X | X | Commissioning | Post Installation | 18-24 months | 609.1 |
| Dimming systems and multi-level scene control systems | X | X | Commissioning | Post Installation | 18-24 months | 609.1 |
| Captive key control devices | X | X | Functional Testing | Post Installation | 18-24 months | 609.1 |
| Chapter 7: Water |
| Water Quality Tests |  |
| Rainwater System |  | X | Field testing and verification | None | 707.16.1 | 707.16.1 |
| Graywater System |  | X | Field testing and verification | None | 708.13.8 | 708.13.8 |
| Chapter 8: IEQ |
| Sound Transmission |  |
| Mechanical and emergency generator equipment located outside buildings or located where exposed to exterior environment. | X | None | Field testing and verification | See Section 807.5.1 | None | 807.5.1 |
| HVAC Background Sound | X | None | Field testing and verification | See Section 807.5.2 | None | 807.5.2 and ANSI/ASA 12.2 |

Section 904

building operations, maintenance and owner education

904.1 General. The building owner shall file a letter with the code official certifying the receipt of record documents and building owner education, operations and maintenance documents. Record documents shall be in accordance with Section 904.2.  The operations and maintenance and building owner education documents shall be in accordance with Sections 904.3 and 904.4 and submitted to the owner prior to the issuance of the Certificate of Occupancy.  At least one copy of these materials shall be in the possession of the owner and at least one additional copy shall remain with the building throughout the life of the structure.

904.1.1 Owner responsibility. Buildings built under this code shall be maintained and operated at the level of performance required by the approved documents

904.1.1.1 Periodic reporting. Where required by Table 302.1, a report confirming that the building is maintained and operated at the level of performance required by the approved documents shall be submitted to the code official at approved intervals.

904.2 Record documents. The cover sheet of the record documents for the project shall clearly indicate that at least one copy of the materials shall be in the possession of the owner and at least one additional copy shall remain with the building throughout the life of the structure. Record documents shall include all of the following:

- Copies of the approved construction documents, including plans and specifications.

- As-built plans and specifications indicating the actual locations of piping, ductwork, valves, controls, equipment, access panels, lighting and other similar components where they are concealed or are installed in locations other than those indicated on the approved construction documents.

3.   A copy of the Certificate of Occupancy.

904.3 Building operations and maintenance documents. The building operations and maintenance documents shall consist of manufacturer’s specifications and recommendations, programming procedures and data points, narratives, and other means of illustrating to the owner how the building, site and systems are intended to be maintained and operated. The following information shall be included in the materials, as applicable to the specific project:

- Directions to the owner or occupant on the manual cover sheet indicating that at least one copy of the materials shall be in the possession of the owner or occupant and at least one additional copy shall remain with the building.

2. Operations and maintenance manuals for equipment, products and systems installed under or related to the provisions of Chapter 4 including, but not limited to, the following, as applicable:

2.1 Vegetative shading, vegetative roofs and natural resource protections and setbacks .

2.2 Water conserving landscape and irrigation systems.

2.3 Stormwater management systems

2.4 Permanent erosion control measures.

3. Operations and maintenance documents for materials, products, assemblies and systems installed under or related to the provisions of this code for material resource conservation in accordance with Chapter 5 including, but not limited to, the following, as applicable:

3.1 Care and maintenance and instructions and recommended replacement schedule for flooring, including, but not limited to, carpeting, walk-off mats and tile.

3.2 Care and maintenance instructions for natural materials including, but not limited to, wood, bio-based materials and stone.

3.3 Available manufacturer’s instructions on maintenance for:

3.3.1. Exterior wall finishes

3.3.2. Roof coverings

3.3.3. Exterior doors, windows and skylights

3.4 Information and recommended schedule for required routine maintenance measures, including but not limited to, painting and refinishing.

3.5 A copy of the service life plan required by Chapter 5.

4.	Operations and maintenance documents for equipment, products and systems installed under or related to the provisions of this code for energy conservation in accordance with Chapter 6 including, but not limited to, the following:

4.1 Heating, Ventilating and Air Conditioning systems including:

4.1.1. Recommended equipment maintenance schedule.

4.1.2. Air filters and fluid filters, including recommended replacement schedule and materials.

4.1.3. Time clocks, including design settings.

4.1.4. Programmable controls and thermostats, including design settings

4.2  Domestic hot water systems including performance criteria and controls.

4.3 Building thermal envelope systems including:

4.3.1. Glazing systems inspection schedule.

4.3.2. Performance criteria for replacements and repairs.

4.3.3. Information and recommended schedule on required routine maintenance measures, including but not limited to, sealants, mortar joints and screens.

4.4 Electrical and lighting systems including:

4.4.1. Technical specifications and operating instructions for installed lighting equipment

4.4.2. Luminaire maintenance and cleaning plan

4.4.3. Lamp schedule, recommended relamping plan, and lamp disposal information.

4.4.4. Programmable and automatic controls, including settings determined during performance verification

4.4.5. Sensors including design settings

4.5  Automatic demand reduction systems

5.	Operations and maintenance documents for equipment, products and systems installed under or related to the provisions of this code for water conservation in accordance with Chapter 7, including, but not limited to the following:

5.1 Domestic fixtures.

5.2 Water regulating devices including faucets and valves.

5.3 Irrigation and rainwater and graywater catchment.

6. 	Operations and maintenance documents for equipment products and systems under or related to the provisions of this code for indoor environmental quality in accordance with Chapter 8, including, but not limited to the following:

6.1 Humidification/dehumidification.

6.2 Green cleaning products, procedures and techniques.

6.3 Recommended window cleaning schedule.

6.4 Ventilation controls.

6.5 Floor finishes.

904.4 Building owner education manual. The owner shall cause to be assembled an informational document on the building, site or structure and systems and sustainable features that are covered by this code and included in the building.  Such information shall be educational in nature and sufficient for future tenants, owners and operators of the building, building site, structure and systems to understand the basic purpose and basis for these systems and features and how they are to be maintained for continued performance.  The education documents shall consist of a statement of performance goals or requirements and a narrative illustrating the reasoning behind the building’s site, features, and systems design. One copy of the owner education manual shall be in the possession of the owner and one additional copy shall remain with the building throughout the life of the structure. Where a whole building life cycle assessment is performed in accordance with Section 304, the data and final report shall be included in the owner education manual.

CHAPTER 10

EXISTING BUILDINGS

SECTION 1001

GENERAL

1001.1 Scope. The provisions of this chapter shall control the alteration, repair, addition, maintenance and operation and change of occupancy of existing buildings and structures.  Existing building sites shall comply with Chapter 11.

1001.2 Building operation and maintenance.  Existing buildings and parts thereof, shall be operated and maintained in conformance with the code edition and zoning or other adopted site development regulations applicable at the time of construction, and as required by Section 102.6.  The owner or the owner’s designated agent shall be responsible for the operation and maintenance of existing buildings. The requirements of this chapter shall not provide the basis for removal or abrogation of fire protection and safety systems and devices in existing structures.

1001.3 Compliance. Alterations, repairs, additions and changes of occupancy to existing structures shall comply with the provisions of this chapter.

1001.4 Building materials, assemblies and systems. Building materials shall comply with the requirements of this section.

1001.4.1 Existing materials, assemblies, configurations and systems. Materials, assemblies, configurations and systems already in use in a building in conformance with requirements or approvals in effect at the time of their erection or installation shall be permitted to remain in use unless determined by the code official to be dangerous to life, health or safety. Where such conditions are determined to be dangerous to the environment, life, health or safety, they shall be mitigated or made safe.

1001.4.2 New and replacement materials, assemblies, configurations and systems. Except as otherwise required or permitted by this code, materials, assemblies, configurations and systems permitted by the applicable code for new construction shall be used. Like materials shall be permitted for repairs and alterations provided that a hazard to life, health or property is not created. Hazardous materials shall not be used where the code for new construction would not permit their use in buildings of similar occupancy, purpose and location.

SECTION 1002

ADDITIONS

1002.1 General. Additions to any building or structure shall comply with the requirements of this code for new construction.  Unaltered portions of the building or structure shall be in accordance with the provisions of the code in force at the time of their construction and shall comply with Section 1003.2.

Aadditions to existing portions or components of the building structure shall be in accordance with the provisions of this code for those portions or components being altered.

- Additions to an existing building or structure shall be made such that the existing building or structure together with the addition are not less conforming with the provisions of this code than the existing building and or structure was prior to the addition.

2.	Additions shall not be permitted to buildings and structures that are located in flood hazard areas, as established in the International Building Code.

Exception: Where an existing building or structure is located such that all habitable space is located not less than 1 foot above the flood elevation, additions complying with Section 402.2.1(1) shall be permitted.

SECTION 1003

ALTERATIONS TO EXISTING BUILDINGS

1003.1 General. Alterations to existing portions or components of buildings shall be in accordance with the provisions of this code for those portions or components being altered.  Unaltered portions and components of the building or structure shall be in accordance with the provisions of the code in force at the time of their construction and shall comply with Section 1003.2.  Alterations shall be such that the existing building or structure is not less conforming to the provisions of this code than the existing building or structure was prior to the alteration, and energy compliance for this purpose shall be evaluated in accordance with Section 602.4. In addition, portions and components that are altered, repaired or replaced shall be in accordance with this section and Sections 1003.2 and 1003.3.

Exception: Where, in the opinion of the code official, there is no significant compromise of the intent of this code, the code official shall have the authority to approve materials and assemblies  that perform in a manner that is at least the equivalent of those being replaced.

1003.2 Minimum energy, HVAC and water requirements. Compliance with Sections 1003.2.1 through 1003.2.3 shall be required.

Exceptions:

1. Materials, assemblies and components regulated by Sections 1003.2.1, 1003.2.2 or 1003.2.3 that are dependent upon properties of other concealed materials, assemblies or system components to function properly and where the properties of the concealed materials, assemblies or components are unknown or insufficient and will not be revealed during construction.

2. Where the application of the requirements of Sections 1003.2.1, 1003.2.2 or 1003.2.3 are determined by the code official to be technically infeasible based upon the existing configuration of spaces, unless the intent of the permit applicant is to reconfigure those spaces or portions thereof.

3. Where a tenant in a multi-tenant building does not have control within that tenant space of a complete system or item, compliance for that complete system or item shall not be required.

1003.2.1 Heating, ventilation and air conditioning. Heating, ventilation and air conditioning systems and equipment shall be in accordance with the following:

- Non-functioning thermostats shall be repaired or replaced.

- Leaking accessible supply air and return ducts shall be sealed with approved sealants. Although the presence of existing duct tape shall not be deemed to indicate noncompliance where a duct is not leaking, duct tape shall not be acceptable for repair of such a leak.

- Outside air dampers, damper controls and linkages controlled by HVAC units shall be in good repair and adjustment.

- Hot water and steam leaks, defective steam traps and radiator control, relief, and vent valves shall not be permitted in any accessible piping.

- Leaking accessible chilled water lines and equipment shall be repaired or replaced.

1003.2.2 Service water systems. Service water systems shall be in accordance with the following:

- The temperature of the supply of hot water for domestic or commercial purposes other than comfort heating shall be set and maintained to provide water at not higher than one hundred ten degrees Fahrenheit at point of use.

Exception: Temperature reset shall not be required where water from a water heater must be higher than one hundred ten degrees Fahrenheit for regular use of a dishwasher or for operating other justifiable equipment, including instantaneous demand water heaters.

- There shall not be leaks in any accessible hot and cold water pipes.

1003.2.3 Motor-driven equipment.  There shall not be leaks in compressed air or pumped water systems.

1003.3 Additional requirements.  Alterations of portions and components of buildings shall comply with Sections 1003.3.1 through 1003.3.9.

Exceptions:

- The total cost of improvements required by Sections 1003.3.1 through 1003.3.9 shall not be required to exceed 10 percent of the costs of the alterations exclusive of land and building site improvements. The costs of alterations shall include costs related to Section 1003.2, but shall not limit its application.

- This section shall not require compliance that exceeds that required for systems regulated by Chapters 6 through 8 of this code.

- Materials, assemblies and components regulated by Sections 1003.3.1 through 1003.3.9 that are dependent upon properties of other concealed materials, assemblies or system components to function properly and where the properties of the concealed materials, assemblies or components are unknown or insufficient and will not be revealed during construction.

- Where the application of the requirements of Sections 1003.3.1 through 1003.3.9 are determined by the code official to be technically infeasible based upon the existing configuration of spaces, unless the intent of the permit applicant is to reconfigure those spaces or portions thereof.

- Where a tenant in a multi-tenant building does not have control within that tenant space of a complete system or item, compliance for that complete system or item shall not be required.

1003.3.1 Energy audit and report. The building owner shall commission a building energy audit and provide copies of the audit report to the local jurisdiction. The audit shall be conducted by persons qualified to perform such audits, as determined by the code official.  The energy audit report shall indicate the improvements listed in Sections 1003.3.2 through 1003.3.9 that the auditor recommends for scoping and prioritizing the modification, replacement or the addition of equipment or systems to improve the energy performance of the building.

Exception: An energy audit and report shall not be required where a building is vacant and has been vacant for a minimum of six months prior to the sale date of the property.

1003.3.2 Metering devices.  Dedicated individual metering devices to facilitate the measurement and verification of energy and water use within the building or space shall be provided for at least one of the following:

- Electrical energy consumption for individual tenant spaces

- Water consumption for individual tenant spaces

- Natural gas or fuel oil consumption for individual tenant spaces

- Lighting loads

- Motor and drive loads

- Chiller part-load efficiency

- Cooling loads

- Economizer and heat recovery loads

- Boiler efficiencies

- Building process systems and equipment loads

- Water consumption for landscape irrigation

1003.3.3  Heating, ventilation and air conditioning. Heating, ventilation and air conditioning systems and equipment shall be in accordance with the following:

  - Time clock and time switch controls that can turn systems off and on according to building occupancy requirements shall be provided and connected to the following HVAC equipment: chillers and other space cooling equipment, chilled water pumps, boilers and other space heating devices, hot water pumps, heat exchanger circulation pumps, supply fans, return fans, and exhaust fans. Where occupant override is provided, it shall be designed with a timer to automatically revert to time clock and time switch controls in not longer than twelve hours.

Exception: A time clock and time switch controls shall not be required for spaces with twenty-four-hour occupancy or containing materials with special atmospheric requirements dependent on twenty-four-hour space conditioning, or where a majority of areas of the building served by the system are under set-back thermostat control, or where manufacturer's specifications stipulate that the system must not be shut off.

  - Functional outside air economizers shall be provided on all cooling systems of more than 6 1/4 tons total cooling capability, 75K Btu/hr., or more than two thousand five hundred cubic feet per minute air flow, provided manufacturer’s guidelines are available for adding the economizer to the existing system.

Exceptions: An outside air economizer shall not be required for  buildings or special uses requiring one hundred percent outside air for ventilation, where the existing system has a water based economizer, where the existing system does not have an outside air intake, where special economizer operations such as, but not limited to, carefully controlled humidity would require more energy use than is conserved, where there is insufficient space to install necessary equipment, where installation of an economizer would require major modifications to the building's life-safety system, or where the existing system is a multi-zone system where the same intake air may be used at the same time for either heating or cooling in different parts of the building.

  - HVAC piping and ducts, including those located above suspended ceilings, shall be insulated to R-values in accordance with this code.

Exception: Additional insulation shall not be required for piping within HVAC equipment, within conditioned space that conveys fluids between sixty degrees Fahrenheit and one hundred five degrees Fahrenheit, piping that is already insulated and the insulation is in good condition, or where the insulation cannot be installed without structural alteration.

  - Furnace combustion units shall have been cleaned and tuned within one year prior to the change of occupancy. Filters shall be replaced in accordance with the furnace manufacturer's recommendations. Where central heat is intended to be replaced with individual electric space heaters, the application for the electrical permit shall include documentation demonstrating that the new electric heaters will not consume more energy than the existing nonelectric heater(s).

  - Boiler systems shall have been cleaned and tuned within one year prior to the change of occupancy.

  - Boilers shall be equipped with an outdoor air lock-out thermostat or a temperature reset control.

  - Chiller systems shall have been cleaned and tuned within one year prior to the change of occupancy.

  - Chillers shall be equipped with an outdoor air lockout thermostat and chilled water reset control.

  - A maximum 5 year phase out plan shall be provided for buildings with existing systems that use CFC-based refrigerants.

  - Where mechanical and electrical systems and equipment are joined with microprocessors that communicate with each other or to a computer, a properly integrated building automation system shall be installed to optimize energy, operations, and indoor comfort. The building automation system shall allow the owner to set up schedules of operation for the equipment and provide equipment optimal start with adaptive learning; provide trim and respond capabilities based on zone demand; ability to monitor energy usage, including the ability to meter electric, gas, water, steam, hot water, chilled water, and fuel oil services; offer economizing based on enthalpy calculation and/or CO2 set point control; offer load shedding when power companies are at peak demand and need; and offer the ability to send alarms to alert building owner, manager, or operator when problems occur due to system failures.

1003.3.4 Service water systems. Service water systems and equipment shall be in accordance with the following:

- Water heater and hot water storage tanks shall have a combined minimum total of external and internal insulation of R-6.

- Accessible hot and cold water supply and distribution pipes shall be insulated to R-values as specified in this code.

- In Seismic Design Categories D, E and F, as established in accordance with the International Building Code, water heater and water storage tanks with a tank capacity of thirty gallons or greater shall be strapped or otherwise secured to a wall, floor, ceiling, or other object that itself is adequately secured to a wall, floor, or ceiling. Water, gas and overflow pipes connected to water tanks shall be similarly secured. Gas water heaters shall have a flexible gas line entering the appliance.

- Circulating pump systems for hot water supply purposes other than comfort heating shall be under timeclock control.  Pumps serving spaces where use requires service hot water available on a twenty-four hour per day basis, such as in hospitals, convalescent homes, motels and hotels, shall not require the use of timeclocks.

- Showerhead, toilet, urinal and faucet flow rates shall be in accordance with this code.

1003.3.5 Lighting. Lighting systems and equipment shall be permitted in accordance with sections 505.2.2.3 and 505.2.4 of the International Energy Conservation Code. [See Code Change EC147-09/10]

1003.3.6 Commercial refrigeration equipment. Commercial refrigeration equipment shall be in accordance with the following:

- Commercial refrigeration equipment shall be cleaned and tuned for efficiency, including, but not limited to, cleaning of condenser coils and evaporators, and replacement of defective or worn door gaskets and seals.

- Low and medium temperature commercial refrigeration cases shall be equipped with doors, strip curtains, or similar devices. Open-tub systems with cooling capacities of less than twenty-five thousand BTU/hour shall not be required to have such doors or strip curtains. Compressor systems shall be modified, as appropriate, to compensate for the reduced cooling load resulting from the installation of doors and strip curtains.

1003.3.7 Motor-driven equipment. Motor-driven systems and equipment shall be in accordance with the following:

- Filters shall be cleaned or replaced.

- Belts and other coupling systems shall be in good repair.

1003.3.8 Swimming pools and spas. Swimming pools and spas and their equipment shall be in accordance with the following:

- Heated swimming pools and spas shall be equipped with a cover for unoccupied hours.

Exception: A cover shall not be required for indoor pools or spas in which water temperature is less than eighty degrees Fahrenheit during time of non-use.

- Pool and spa recirculation pumps shall be under timeclock control.

- Heaters shall be cleaned and tuned for efficiency within one year prior to the change of occupancy.

1003.3.9 Unconditioned attic insulation.  In buildings with three or fewer stories above grade plane, ceiling insulation with a minimum R-value as required by this code shall be installed in accessible attic spaces that are directly above conditioned spaces. For the purposes of this section, accessible attic space shall be the space between a ceiling joists and roof rafters where the vertical clear height from the top of a ceiling joist or the bottom chord of a truss, to the underside of the roof sheathing at the roof ridge, is greater than twenty-four inches. Where the required R-value insulation cannot fit in the attic space, the maximum amount of insulation compatible with available space and existing uses shall be installed.

SECTION 1004

CHANGE OF OCCUPANCY

1004.1 Change of occupancy. Where a change in occupancy of a building or tenant space places it in a different division of the same group of occupancy or in a different group of occupancies, as determined in accordance with the provisions of the International Building Code, compliance with Section 1003.2 shall be required.  Altered portions of, and additions to, existing buildings that are not a result of change of occupancy requirements, shall comply with other sections of this chapter, as applicable.

Exception:  Historic buildings in accordance with Section 1005 shall not be required to comply with Section 1004.

SECTION 1005

HISTORIC BUILDINGS

1005.1 Historic buildings. The provisions of this code relating to the construction, repair, alteration, addition, restoration and movement of structures, and change of occupancy, where each individual provision is evaluated separately on its own merit, shall not be mandatory for historic buildings for any of the following conditions:

1. Where implementation of that provision would change the visible configuration of building components in a manner that is not in keeping with the buildings historic nature, as determined by the code official,

2. Where compliance with that provision would produce a conflict with a building function that is fundamental to the historic nature of the building, or

SECTION 1006

RELOCATED STRUCTURES

1006.1 Conformance. Structures relocated into or within the jurisdiction, other than historic buildings, shall comply with the provisions of Section 1003.2.

SECTION 1007

JURISDICTIONAL REQUIREMENTS

1007.1 General.  Sections 1007.2 and 1007.3 shall be mandatory and Section 1007.4 shall be enforced only where specifically indicated by the jurisdiction in Table 302.1.

1007.2 Demolition. Where buildings, structures or portions thereof are deconstructed or demolished, a minimum of 50 percent of materials shall be diverted from landfills and incineration.  Documentation of the total materials in buildings, structures and portions thereof to be deconstructed or demolished and materials to be diverted, and evidence of diversion, shall be provided. Material quantities shall be indicated and calculated by weight or volume, but not by both.

1007.3 Sale of existing buildings and tenant spaces. Buildings and tenant spaces that are sold shall comply with Sections 1003.2 and 1003.3 within 1 year of sale.

1007.4 Evaluation and certification of existing buildings and building sites. Where a permit application is accepted by a jurisdiction for the evaluation of an existing building and building site in accordance with the requirements of this code as applicable to a new project, and this code does not otherwise require conformance, evaluation shall be in accordance with the requirements of this section. Project electives in accordance with Table 303.1 shall be included in the evaluation of the existing building.

1007.4.1 Certificate of conformance. Where conformance with the requirements of this code as applicable to a new building is verified by the code official for an existing building and building site, a certificate shall be issued indicating conformance with this code, as modified by the limitations contained in Sections 1007.4.2 through 1007.4.3.2..

1007.4.2 Specific exclusions. Where evidence of compliance is not available, existing buildings evaluated under Section 1007.4 shall not be subject to the requirements of Section 806. Provisions of this code related to the projects construction phase, including Sections 402.3.1, 402.3.5, 402.3.6, 502.1, 506 and 803.1, and other sections as approved by the code official,, shall not be required for buildings evaluated under Section 1007.4. Where buildings do not comply with the aforementioned sections, the certification shall specifically list the sections for which compliance has not been required or verified.

1007.4.3 Existing concealed construction. Existing concealed construction in buildings regulated by Section 1007.4 shall be in accordance with Sections 1007.4.3.1 and 1007.4.3.2.

1007.4.3.1 Previously approved documents. Previously approved construction documents for the initial construction of an existing building and, where possible, description of changing uses and major upgrades over the building’s lifetime for which a certificate of occupancy was previously issued shall be deemed an acceptable indication of materials, assemblies and equipment in concealed spaces, except where field inspection reveals sufficient evidence suggesting noncompliance, subject to the evaluation of the code official.

1007.4.3.2 Previously approved documents not available. Where previously approved construction documents for the initial construction of an existing project are not available, materials, assemblies and equipment in spaces in existing buildings and existing portions thereof that are concealed, including, but not limited to, materials in spaces within walls and floor/ceiling assemblies, shall be exposed and spot checked in limited areas as determined by the code official.

CHAPTER 11

EXISTING BUILDING SITE DEVELOPMENT

SECTION 1101

GENERAL

1101.1 Scope. The provisions of this chapter shall control the alteration, repair, maintenance and operation of existing building sites and the alteration to building site improvements where additions are made to, or changes of occupancy occur within, the existing buildings on the site.

1101.2 Operation and maintenance.  Building sites shall be operated and maintained in conformance with the code edition under which the site improvements were installed.  The owner or the owner’s designated agent shall be responsible for the operation and maintenance of building sites. To determine compliance with this section, the code official shall have the authority to require a building site to be reinspected. The requirements of this chapter shall not provide the basis for removal or abrogation of protections or systems from existing building sites.

1101.3 Compliance. Alterations and repairs to building sites shall comply with the provisions of this code. Where differences occur between the provisions of this code and the provisions of other locally adopted land use, zoning or site development regulations, the provisions of the most restrictive code or regulation shall apply.

Exception. The following need not comply with Chapter 4, provided that the area of impervious surfaces on the building site is not increased:

- Restriping of parking lots provided there is not a change in the number of parking spaces;

- Replacement of hardscape, structures and vegetation with materials that duplicate the materials in the permitted plans and specifications

1101.4 Building site materials, systems and landscaping.   Building materials used for building site development shall comply with the requirements of this section.

1104.4.1 Existing materials, assemblies, configurations and systems. Materials and systems already in use on a building site in conformance with the requirements or approvals in effect at the time of their installation shall be permitted to remain in use unless determined by the code official to be dangerous to the environment, life, health or safety.    Where such conditions are determined to be dangerous to the environment, life, health or safety, they shall be mitigated or made safe.

Existing buildings and site improvements located within or located closer to protected areas than permitted by Section 402.2 but that are in conformance with the requirements or approvals in effect at the time of their installation shall be permitted to remain in use unless determined by the code official to be dangerous to the environment, life, health and safety of the community and the occupants of the building site.  Where such conditions are determined to be dangerous to the environment, life, health or safety, they shall be mitigated or made safe.

1101.4.2 New and replacement materials, assemblies, configurations and systems. Except as otherwise required or permitted by this code, materials, assemblies, configurations and systems permitted by the applicable code for new construction shall be used. Like materials shall be permitted for repairs and alterations provided no hazard to the environment, life, health or property is created. Hazardous materials shall not be used where the code for new construction would not permit their use at building sites of similar occupancy, purpose and location.

SECTION 1102

ADDITIONS

1102.1 General. Additions to any building site improvements shall comply with the requirements of this code for new construction.  Unaltered portions of a building site shall be in accordance with the provisions of the code in force at the time of their construction.

Where additions to a building, or additions to building site improvements result in the alteration of existing portions or improvements of the building site, those alterations shall comply with this section and Section 1103.

Additions to an existing building site shall be made to ensure the following:

- Existing building site improvements together with the additional or expanded improvements are not less conforming with the provisions of this code than the existing building site was prior to the addition, and;

- Where additions to any building reduces, or requires alteration to, building site improvements, the alterations to the building site together with unaltered site improvements shall not be less conforming to the provisions of this code prior to the addition to the building or structure.

SECTION 1103

ALTERATIONS TO EXISTING BUILDING SITES

1103.1 General. Alterations to existing portions or site improvements on building sites shall be in accordance with the provisions of this code for those portions or building site improvements being altered.  Unaltered portions and site improvements of the building site shall be in accordance with the provisions of the code in force at the time of their construction. Alterations shall be such that the existing building site is no less conforming with the provisions of this code than the existing building site was prior to the alteration.

Unaltered portions and site improvements of a building site shall be in accordance with the provisions of the code in force at the time of their construction or preservation.

Exception: Where, in the opinion of the code official, there is no significant compromise of the intent of this code, the code official shall have the authority to approve materials and assemblies that perform in a manner that is at least the equivalent of those being replaced.

1103.2 Changes to hardscapes and surface vehicle parking.  Where existing hardscapes that do not conform to the requirements of 404.2 are altered, the alterations shall comply with the provisions of this code.  In addition, not less than 25 percent of the remaining hardscape shall be altered to comply with the provisions of this code.

Where existing vehicle surface parking lots that do not comply with Section 403.4 are altered to rearrange parking space configuration or to increase the number of parking spaces, the altered parking lot shall comply with Section 403.4.  In addition, if the existing building site does not have the number of short term bicycle parking spaces required by Section 403.3, additional short term bicycle parking complying with Section 403.3 shall be provided in order that the building site subsequent to the alternation complies with Section 403.3 for short term bicycle parking.

SECTION 1104

CHANGE OF OCCUPANCY

1104.1 Conformance. Where a change in the use or occupancy of a building or tenant space places it in a different division of the same group of occupancy or in a different group of occupancies, as determined in accordance with the provisions of the International Building Code, compliance with Sections 1104.2 shall be required.  Altered portions of, and additions to, existing buildings and existing building sites that are not a result of change of occupancy requirements, shall comply with other sections of Chapter 10 and this chapter.

1104.2 Building site improvements.  Where a change in occupancy results in an increase in the occupant load of the building, bicycle parking shall comply with the following:

1.  	Short term bicycle parking spaces shall be provided in accordance with Section 403.3 equivalent to a new building of the new occupancy.

2.  	Where the existing building and building site have parking for motorized vehicles, long term bicycle parking shall be provided in accordance with Section 403.3 equivalent to a new building of the new occupancy.    Where the existing building does not contain covered parking spaces for vehicles, only 25 percent of the long term bicycle parking needs to be covered.

SECTION 1105

HISTORIC BUILDING SITES

1105.1Historic building sites.  The provisions of this code relating to the construction, repair, alteration, addition, and restoration of building sites and site improvements, where each individual provision is evaluated separately on its own merit, shall not be mandatory for historic building sites for any of the following conditions:

- Where implementation of that provision would change the visible configuration of building site improvements in a manner that is not in keeping with the building site’s  historic nature, as determined by the code official,

- Where compliance with that provision would produce a conflict with a building site function that is fundamental to the historic nature of the building site, or

- Where such building sites are judged by the code official to not constitute a distinct environmental hazard.

CHAPTER 12

REFERENCED STANDARDS

This chapter lists the standards that are referenced in various sections of this document. The standards are listed herein by the promulgating agency of the standard, the standard identification, the effective date and title, and the section or sections of this document that reference the standard. The application of the referenced standards shall be as specified in Section 102.4.

Air Conditioning, Heating and Refrigeration Institute

2111 Wilson Boulevard, Suite 500

Arlington, VA 22201

Standard 	Referenced

reference	 in code

number 	Title 				section number

870—2009	Direct Geoexchange Heat Pumps. . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . .  . . . . . . . . . .Table 613.5.1.3

American Public Health Association

800 I Street NW

Washington, DC 20001

Standard 	Referenced

reference	 in code

number 	Title 				section number

2005	Standard Methods for Examination of Water and Waste Water-21st Edition . . . . .. . . . 202, .707.16.1.1

California Air Resource Board

1001 “I” Street, P. O. Box 2815

Sacramento, CA 9512

Standard 											             Referenced

reference 	in code

number 	Title 				section number

February 1, 2008		California Air Resources Board, Architectural Coatings Suggested Control Measures

February 1, 2008.	Table 806.3(1)

Acoustical Society of America

Suite 1N01

2 Huntington Quadrangle

Melville, NY 11747-4502

Standard 	Referenced

reference	 in code

number 	Title	 			section number

ANSI/ASA S12.2-2008	Criteria for Evaluating Room Noise. 	Table 903.1

American Society of Mechanical Engineers

Three Park Avenue

New York, NY 10016-5990

Standard 	Referenced

reference	 in code

number 	Title	 			section number

A112.18.1/

CSA B125.1—2010	Plumbing Supply Fittings. 	Table 702.1, 702.2

American Society of Heating, Refrigerating and Air Conditioning Engineers, Inc.

1791 Tullie Circle

Atlanta, GA 30329-2305

Standard	Referenced

reference	 in code

number 	Title 				section number

55-2004			Thermal Environmental Conditions on Human Occupancy……………………………   803.2, C102.6.1

62.1-2010		Ventilation for Acceptable Indoor Air Quality………………………………………………607.3, C102.6.1

90.1-2010		Energy Standard for Buildings Except Low-rise Residential Buildings

(ANSI/ASHRAE/IESNA 90.1-2007)……………………………………………………613.5.1.1, 613.5.1.2

140-2010			Standard Method of Test for the Evaluation of Building Energy Analysis Computer Programs…………………………………………………………………………………………………602.5.2

189.1—2009		Standard for the Design of High Performance Green Buildings, Except Low Rise Residential

Buildings……………………………………………………………………………………302.1, Table 302.1

American Society of Mechanical Engineers

Three Park Avenue

New York, NY 10016-5990

Standard	Referenced

reference	 in code

number 	Title 				section number

1016—2010		Performance Requirements for Automatic Compensating, Valves for Individual

Showers and Tub/Shower Combinations	Table 702.1

ASTM International

100 Barr Harbor

West Conshohocken, PA 19428-2959

Standard 											             Referenced

reference 	in code

number 	Title 				section number

D2729—03		Standard Specification for Poly(Vinyl Chloride) PVC Sewer Pipe and Fittings……………Table 406.2.6

D2974—07a		Standard Test Methods for Moisture, Ash, and Organic Matter of Peat and other Organic Soils……………………………………………………………………………………………………  406.4.2.1

D3385—09		Standard Test Method for Infiltration Rate of Soils in Field Using Double-Ring Infiltrometer…406.4.2.2

D3960—05		Standard Practice of Determining Volatile Organic Compound (VOC) Content of Paints & Related Coatings……………………………………………………………… ……………………………806.2, 806.3

D5093-02(2008)		Standard Test Method for Field Measurement of Infiltration Rate Using Double-Ring Infiltrometer With Sealed-Inner  Ring…………………………………………………………………………………  406.4.2.2

D6886—03		Standard Test Method for Specification of the Volatile Organic Compounds

(VOCs) in Low VOC Content Waterborne Air-Dry Coatings by Gas Chromatography	503.2.4

E90-04 			Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building

Partitions and Elements…………………………………………………807.2; 807.3 807.4.1, 809.2, 809.3

E1332-90 (2003)		Standard Classification for the Determination of Outdoor-Indoor Transmission Class…….………807.2

E1509—04		Standard Specification for Room Heaters, Pellet Fuel-Burning Type……………………………   804.1.6

E1602—03		Standard Guide for Construction of Solid Fuel Burning Masonry Heaters……………………………………………………………………………………………………804.1.7

E1903—97(2002)		Standard Guide for Environmental Site Assessments: Phase II Environmental

Site Assessment Process………………………………………………………………………………407.2.4

E1980—01		Standard Practice for Calculating Solar Refluctance Index of Horizontal

And Low-Sloped Opaque Surfaces………………………………………   02, 404.1.1, 404.2.1, 404.3.1.2

E2112—07		Standard Practice for Installation of Exterior Windows, Doors and Skylights	504.3.3

E2396—05		Standard Test Method for Saturated Water Permability Granular Drainage Media

[Falling Head Method] for Green Roof Systems…………………………………………………………	406.6

E2397—05		Standard Practice for Determination of Dead Loads and Live Loads associated with Green

Roof Systems………………………………………………………………………………………………	406.6

E2398—05		Standard Test Method for Water Capture and Media Retention of Geocomposite Drain Layers

For Green Roof Systems…………………………………………………………………………………	406.6

E2400—06		Standard Guide for Selection, Installation and Maintenance of Plants for Green Roof

Systems……………………………………………………………………………………………………	406.6

F405—05			Standard Specification for Corrugated Polyethylene (PE) Pipe and Fittings………………	Table 405.2.6

F1488—09		Standard Specification for Coextruded Composite Pipe……………………………………Table 406.2.6

California Code of Regulations

Department of Industrial Relations

Office of the Director

455 Golden Gate Avenue

San Francisco, CA 94102

Standard 	Referenced

reference 	in code

number 	Title 				section number

Section 93120-Title 17	California Code Regulations, Airborne Toxic Control

Measure to Reduce Formaldehyde Emissions.	806.1

Cool Roof Rating Council

1610 Harrison Street

Oakland, CA 94612

Standard 	Referenced

reference 	in code

number 	Title 				section number

CRRC-1			Cool Roof Rating Council Standard……………………………………………………404.3.1.1, 404.3.1.2

Canadian Standards Association

5060 Spectrum Way

Mississauga, Ontario, Canada L4N 5N6

Standard 	Referenced

reference 	in code

number 	Title 				section number

CAN/CSA B366.1-2009	Solid-Fuel-Fired Central Heating Appliances………………………………………………………  804.1.6

CSA Z21.50/CSA 2.22-2003	Vented Gas Fireplaces…………………………………………………………………………………804.1.3

CSA Z21.88a/CSA 2.33a	ANSI/CSA Standard for Vented Gas Fireplace Heaters……………………………………………804.1.3

California Department of Health Services

Office of Regulations

P.O. Box 997413, MS 0015

Sacramento, CA 95899-7413

Standard 	Referenced

reference 	in code

number 	Title 				section number

CA/DHS/EHLB/R-174-2004-1	Standard Practice for the Testing of Volatile Organic Emissions from Various Sources

Using Small-Scale Environmental Chambers including Addendum ……2004-1, 806.2, Table 806.2(2),

806.3, Table 806.3(2) 806.4, 806.5, 806.6, 809.2.4

U.S. Department of Commerce

National Institute of Standards and Technology

1401 Constitution Avenue NW

Washington, DC 20230

Standard 	Referenced

reference 	in code

number 	Title 				section number

NOAA	National Oceanic and Atmospheric Administration Annual Mean Sunshine Percentage

Table………………………………………………………………………………………………Table 609.5

PS1—09 	Structural Plywood……………………………………………………………………………………… 806.1

PS2—10	Performance Standard for Wood-Based Structural-Use Panels. …………………………………  806.1

U.S. Department of Energy

C/o Superintendent of Documents

U.S. Government Printing Office

Washington, DC 20402-9325

Standard 	Referenced

reference 	in code

number 	Title 				section number

10 CFR Part 431	Sub-Part K, Appendix A…………………     Table 609.8.1.1(1), Table 609.8.1.1(2), Table 609.8.1.1(3)

DOE/CH/10093-4-10/86	Appendix C of NREL “Wind Energy Resource Atlas of United States”………………………………611.3

Environmental Protection Agency

Ariel Rios Building

1200 Pennsylvania Avenue, NW

Washington, DC 20460

Standard 											             Referenced

reference 	in code

number 	Title 				section number

40 CFR, 	EPA Standards of Performance for New Residential Wood Heaters	804.1.5

Part 60 Subpart AAA

EPAct 2005	Environmental Protection Act 2005.	608.1, 609.8.1.1

ENERGY STAR	Energy Star. 	202, 607.2.2.3, 607.2.3.1, 610.2.3, 610.3.1, 610.3.2, 613.5.1.1, 613.5.1.2, 609.2,

Table 702.1, Table 702.1.1(2), 702.6.1, 702.6.2, 702.6.4, C102.2

Water Sense Feb-2007	High Efficiency Toilet Specification……………………………Table 702.1, Table 702.1.1(3)

US EPA Method 24		Determination of Volatile Matter Content, Water Content, Density, Volume Solids

And Weight Solids of Surface Coatings	806.2

The International Electrotechnical Commission

Central Office

3, rue de Varembe’

P. O. Box 131

Ch-1211 Geneva 20

Switzerland

Standard 											             Referenced

reference 	in code

number 	Title 				section number

IEC, 	Standard on Efficiency classes for low voltage AC motors…………………………610.2.1.1, 610.2.2.2

60034-30-2009

International Code Council, Inc.

500 New Jersey Avenue, NW

6th Floor

Washington, DC 20001

Standard 	Referenced

reference 	in code

number 	Title 				section number

IBC-12	International Building Code® 	101.2., 102.4.1; 102.4.12.1, 102.6, 109.2

201.3, 202, 304.1, 402.2.1.1, 403.3.2, 403.4, 404.2.2,

406.2.1, 606.1.3.3; 609.3, 610.2, 611.3.1.2, 707.12.7.4,

708.12.6.4, 710.6.1; 710.7,

803.1.2.1; 804.1.7, 1002.1, 1003.3.4, 1004.1, 1104.1

IFGC-12	International Fuel Gas Code®	102.4.2, 201.3, 604.4.1, 610.2, 804.1.2

IMC-12	International Mechanical Code®	102.4.3, 201.3, 202, 604.4.2, 607.3, 607.6.1,

607.9.1, 610.2, 612.1.2.1, 803.1.2.1, 803.3, 804.1.2

IPC-12 	International Plumbing Code® 	102.4.4, 201.3, 306, 608, 610.2; 611.2,

Table 702.1, 702.11, 704.1.3, 704.2, 707.5, 707.11

705.2, 707.3, 707.12.3.2, 707.12.4.1, 707.12.4.3, 707.12.7.3,

707.12.7.5, 707.12.7.6

, 707.12.7.8, 707.12.7.11, 707.12.11; 707.12.11.3;

707.12.12.1; 707.12.12.2, 707.12.12.3; 707.13.1; 707.13.2, 707.13.3,

707.13.4, 708, 708.3, 708.5; 708.10, 708.12.1.1, 708.12.2,

708.12.3.1, 708.12.3.2, 708.12.3.3, 708.12.6.5, 708.12.6.6,

708.12.6.8, 708.12.6.11, 708.12.8, 708.12.9,

708.12.9.3, 708.12.10.1, 708.12.10.2, 708.12.10.3,

708.13.1, 708.13.2,

708.13.3, 708.13.4, 709.3, 709.4, 709.7, 709.8, 707.9.1.1;

709.1.2, 709.9.1.3, 709.10.1,

709.10.2, C102.5.1

IPMC-12	International Property Maintenance Code®	102.4.5, 102.6

IFC-12	International Fire Code®	102.4.6, 102.6, 201.3

IECC-12	International Energy Conservation Code®	102.4.7, 201.3, 202, 404.2, 404.3, Table 405.1.1,

407.4.1, 407.4.2, 407.4.3, 407.4.4, 602.1, 602.2,

602.3.2.2, 603.2, 603.3, Table 603.3, 603.4,

606.1, 606.1.1, 606.1.3, 606.1.3.1, 606.1.4.3,

607.1, 607.2.1, 607.2.3, 607.4, 607.4.1, 607.6,

607.8, 607.9, 607.9.1, 608.2.1,

608.3, 608.4, 609.1, 609.7, 609.9, 609.10, 610.2,

612.1, 612.1.3, 612.2, 612.2.2, 612.2.3.1

612.2.3.3, 612.3, 612.3.2, 613.5.1.1, 613.5.1.2, 613.5.3,

613.5.4.1, 1003.3.5, 1004.1, 1104.1

IWUIC-12	International Wildland-Urban Interface®	102.4.8

ICC-PC-12	International Performance Code®	102.4.9

IEBC-12	International Existing Building Code®	102.4.10, 102.6

IRC-12	International Residential Code®…………………………………………………………………   202; 804.2

IZC-12	International Zoning Code®	102.4.11

ICC-700-08	ICC 700 National Green Building Standard®	102.4.2, Table 102.4.12; 102.4.12.1; 302.1; Table 302.1

Illuminating Engineering Society of North America

120 Wall Street, 17th floor

New York, NY 10005-4001

Standard 	Referenced

reference 	in code

number 	Title 				section number

TM-15-07 	Addendum A…………………………………………………Table 405.2, Table 405.3(1), Table 405.3(2)

International Organization for Standardization

ISO Central Secretariat

1 ch, de la Voie-Creuse, Case Postale 56

CH-1211 Geneva 20, Switzerland

Standard 	Referenced

reference 	in code

number 	Title 				section number

13256-1-1998		Water to Air Closed Loop…………………………………………………………………… Table 613.5.1.3

13256-1-1998		Water to Air Open Loop………………………………………………………………………Table 613.5.1.3

13256-2-1998		Water to Water Closed Loop………………………………………………………………   Table 613.5.1.3

13256-2-1998		Water to Water Open Loop…………………………………………………………………  Table 613.5.1.3

ISO/IEC 17025-2005	General Requirements for the Competence of Testing and Calibration

Laboratories…………………806.2, Table 806.2(2), 806.3;, 806.4, 806.5, 806.6, 809.2.4, 2004-11

National Renewable Energy Laboratory

1617 Cole Boulevard

Golden, CO 80401-3305

Standard 	Referenced

reference 	in code

number 	Title 				section number

SERI TR-642-761 	Simplified Clear Sky Model for Direct and Diffuse Insolation on Horizantal Surfaces……………611.2

National Fire Protection Association

1 Batterymarch Park

Quincy, MA 02269

Standard 	Referenced

reference 	in code

number 	Title 				section number

NFPA 70-2011 	National Electrical Code.	604.4.4, 611.2.3.2, 611.3.3.1

NFPA 72-2010	National Alarm and Signaling Code	710.6.2

NSF International

789 Dixboro Road

Ann Arbor, MI 48105

Standard 	Referenced

reference 	in code

number 	Title 				section number

NSF/ANSI 44-09		Residential Cation Exchange Water………………………………………………………………… 704.1.2

NSF/ANSI 50-09		Equipment for Swimming Pools, Spas, Hot Tubs, and other Recreational

Water Facilities……………………………………………………………………………………… 708.12.7.1

NSF/ANSI 58-09		Reverse Osmosis Drinking Water Treatment Systems………………………………………………704.2

NSF/ANSI 61-09		Drinking Water Systems Components – Health Effects…………………………………………… 707.16

NSF/P151-95		Health Effects from Rain Water Catchment Systems Components…………………………  707.12.1.1

South Coast Air Quality Management District

21865 Capley Drive

Diamond Bar, CA 91765

Standard 	Referenced

reference 	in code

number 	Title 				section number

SCAQMD Method 302-91	Distillation of Solvents from Paints, Coatings and Inks, South Coast Air Quality

(Revised 1993)	Management District	803.2

SCAQMD Method 303-91

(Revised 1993)	Determination of Exempt Compounds, South Coast Air Quality Management District	803.2

SCAQMD Method 304-91

(Revised February 1996)	Determination of Volatile Organic Compounds (VOC) in Various

Materials, South Coast Air Quality Management District.	803.2

SCAQMD Method 316A-92	Determination of Volatile Organic Compounds (VOC) in Materials Used for

Pipes and Fittings.	803.2

SCAQMD Method 316B-92	Determination of Volatile Organic Compounds (VOC) In Adhesives containing

Cyanoacrylates	803.2

SCAQMD Rule 1168	Adhesives and Sealant Applications……………………………………………………………………  806.2

Sustainable Forest Initiative, Inc.

900 17th Street, NW, Suite 700

Washington, DC 20006

Standard 	Referenced

reference 	in code

number 	Title 				section number

SFI-2010-2014		Sustainable Forest Initiative 2010-2014………………………………………………………………503.2.4

Sheet Metal & Air Conditioning Contractors National Assoc. Inc.

4021 Lafayette Center Road

Chantilly, VA 22021

Standard 											             Referenced

reference 	in code

number 	Title 				section number

2010		SMACNA HVAC Air Duct Leakage Test Manual (1st Edition).	606.5.2, 606.5.4

The Masonry Society

3970 Broadway, Unit 201-D

Boulder, CO 80304-1135

Standard 											             Referenced

reference 	in code

number 	Title 				section number

0302-2011		Standard Method for Determining the Sound Transmission Class Rating for

Masonry Walls	…………………………………………………………………………..809.3, 809.5.1

Underwriters Laboratories Inc.

333 Pfingsten Road

Northbrook,  IL 60062

Standard 											              Referenced

reference 	in code

number 	Title 				section number

UL 1482-2011		Room Heaters, Solid Fuel Type.	804.1.5

US Composting Council

1 Comac Loop 14 B1

Rokonkoma, NY 11779

Standard 											             Referenced

reference 	in code

number 	Title 				section number

TMECC 05.7a		Test Method for the Examination of Composting and Compost.	406.4.2.1

United States Department of Agriculture

Office of Energy Policy and New Uses

Room 361, Reporters Bldg.

300 Seventh Street, SW

Washington, DC 20024

Standard 											             Referenced

reference 	in code

number 	Title 				section number

7 CFR Part 2902-Rev. 1/1/06	Guidelines for designating Bio-based products for Federal Procurement.	503.2.4

APPENDIX A

OPTIONAL ORDINANCE

The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.

The International Codes are designed and promulgated to be adopted by reference by ordinance. Jurisdictions wishing to adopt the International Green Construction Code® (IgCC®) as enforceable regulations of sustainable construction practice governing structures and premises should ensure that certain factual and fiscal information is included in the adopting ordinance at the time adoption is being considered by the appropriate governmental body.

The following sample adoption ordinance addresses several key elements of a code adoption ordinance, including the information required for insertion into the code text and an evidentiary-based adoption structure contain bonding requirements tied to the issuance of building permits, certificates of occupancy and the compliance verification process, a concept already familiar to jurisdictions’ master development plans for larger-scale, Planned-Unit Developments (PUD’s).

Most importantly, this Optional Ordinance ‘B’ intends to open the dialogue among stakeholders, and give jurisdictions a place to start an fiscal and evidentiary-based adoption structure utilizing performance bonding requirements tied to the compliance verification process. The bonding requirement is designed to ensure that the project complies with the IgCC. The bond is held by the jurisdiction. Bond amounts are set at a percentage of total cost of the building, based on local economic and geo-centric requirements overseen by jurisdictional authorities, and tied to square footage.

SAMPLE ORDINANCE FOR ADOPTION OF

THE INTERNATIONAL GREEN CONSTRUCTION CODE

ORDINANCE NO.________

An ordinance of the [JURISDICTION] adopting the International Green Construction Code®, regulating and governing the impact of buildings and structures on the environment in the [JURISDICTION]; providing for the issuance of permits and collection of fees therefore; repealing Ordinance No. ______ of the [JURISDICTION] and all other ordinances and parts of the ordinances in conflict therewith.

The [GOVERNING BODY] of the [JURISDICTION] does ordain as follows:

Section 1. That a certain document, three (3) copies of which are on file in the office of the [TITLE OF JURISDICTION’S KEEPER OF RECORDS] of [NAME OF JURISDICTION], being marked and designated as the International Green Construction Code, including Appendix Chapters [FILL IN THE APPENDIX CHAPTERS BEING ADOPTED] (see International Green Construction Code Section 101.2.1), as published by the International Code Council, be and is hereby adopted as the Green Construction Code of the [JURISDICTION], in the State of [STATE NAME] for regulating and governing the impact of buildings and structures on the environment as herein provided; providing for the issuance of permits and collection of fees thereof; and each and all of the regulations, provisions, penalties, conditions and terms of said Green Construction Code on file in the office of the [JURISDICTION] are hereby referred to, adopted, and made a part hereof, as if fully set out in this ordinance, with the additions, insertions, deletions and changes, if any, prescribed in Section 2 of this ordinance.

Section 2. The following sections are hereby revised:

Section 101.1. Insert: [NAME OF JURISDICTION]

Table 302.1. Insert: [JURISDICTIONAL REQUIREMENTS].

Section 3. That Ordinance No. ______ of [JURISDICTION] entitled [FILL IN HERE THE COMPLETE TITLE OF THE ORDINANCE OR ORDINANCES IN EFFECT AT THE PRESENT TIME SO THAT THEY WILL BE REPEALED BY DEFINITE MENTION] and all other ordinances or parts of ordinances in conflict herewith are hereby repealed.

Section 4. That if any section, subsection, sentence, clause or phrase of this ordinance is, for any reason, held to be unconstitutional, such decision shall not affect the validity of the remaining portions of this ordinance. The [GOVERNING BODY] hereby declares that it would have passed this ordinance, and each section, subsection, clause or phrase thereof, irrespective of the fact that any one or more sections, subsections, sentences, clauses and phrases be declared unconstitutional.

Section 5. That nothing in this ordinance or in the Green Construction Code hereby adopted shall be construed to affect any suit or proceeding impending in any court, or any rights acquired, or liability incurred, or any cause or causes of action acquired or existing, under any act or ordinance hereby repealed as cited in Section 3 of this ordinance; nor shall any just or legal right or remedy of any character be lost, impaired or affected by this ordinance.

Section 6. That the [GOVERNING BODY] hereby directs and causes for all privately owned nonresidential projects of at least [insert] square feet, a performance bond, irrevocable letter of credit from a financial institution authorized to do business in the jurisdiction, or evidence of cash deposited in an escrow account in a financial institution in the jurisdiction, to be provided to the jurisdiction, with the bond, LOC or escrow, “due and payable prior to receipt of certificate of occupancy.”

- A commercial applicant who applies for an incentive described in Section 7 shall provide a performance bond which shall be due and payable upon approval of the first building construction permit application.

- On or before [EFFECTIVE DATE], all applicants for construction governed by Section 1 shall provide a performance bond, which shall be due and payable prior to issuance of a certificate of occupancy.

- For the purpose of compliance with subsections (a) and (b) of this section, in lieu of the bond required by this section, the [GOVERNING BODY] may accept an irrevocable letter of credit from a financial institution authorized to do business in the [JURISDICTION] or evidence of cash deposited in an escrow account in a financial institution in the [JURISDICTION] in the name of the licensee and the [JURISDICTION]. The letter of credit or escrow account shall be in the amounts required by subsection (d) of this section.

- The amount of the required performance bond under subsection (a) of this section shall be 1 percent of the incentive provided.

- The amount of the required performance bond under subsection (b) of this section shall be:

- For a project not exceeding 150,000 square feet of gross floor area, 2 percent of the total cost of the building;

(2) 	For a project from 150,001 to 250,000 square feet of gross floor area, 3 percent of the total cost of the building; and.

(3) 	For a project exceeding 250,000 square feet building of gross floor area, 4 percent of the total cost of the building.

- The maximum amount of a performance bond shall be $3 million.

- All or part of the performance bond shall be forfeited to the [JURISDICTION] and deposited in a Green Building Fund if the building fails to meet the verification requirements described in sub-parts (1) and (2) below.

- Publicly-owned, private leasing of public property, publicly financed buildings, and tenant improvements.

- Privately-owned buildings.  Any new construction or substantial improvement of a nonresidential privately-owned project with [insert] square feet of gross floor area or more shall:

  - On or before [EFFECTIVE DATE], submit to the Department of Buildings, as part of any building construction permit application, a green building checklist documenting the green building elements to be pursued in the building construction permit.

  - Within 365 days (1 year)  of the receipt of a certificate of occupancy, be verified “in compliance” with the requirements of this ordinance through:

    - An agency of the [JURISDICTION] government; or

    - Third-party entities which meet criteria to be established by the [GOVERNING BODY] by rulemaking within 180 days of the effective date of this ordinance;

as having fulfilled or exceeded the requirements of the International green Construction Code.

- The [JURISDICTION] shall draw down on the bond funds if the required green building verification is not provided within 730 days (2 years) after issuing the first certificate of occupancy.

- The [GOVERNING BODY] shall promulgate rules to establish additional requirements for the drawing down or return of performance bonds.

Section 7. Incentives.

(a) Within 180 days of the effective date of this ordinance, the [GOVERNING BODY] shall establish an incentive program to promote early adoption of green building practices by applicants for building construction permits for commercial buildings. The incentive program shall be funded by funds deposited in the Green Building Fund, subject to the availability of funds. As part of the incentive program, the [GOVERNING BODY] shall establish a [[PROPERTY TAX INCENTIVE or INCENTIVES PROGRAM]] for Qualifying Green Building Properties, and [[MAY PROVIDE GRANTS]] to help defray costs associated with the early adoption of the green building practices of the International green Construction Code.

Section. 8. Green Building Fund.

(a) There is established a fund designated as the Green Building Fund, which shall be ENROLLED ORIGINAL Codification [JURISDICTION] of Columbia Official Code, 2001 Edition 8 West Group Publisher, 1-800-328-9378, separate from the General Fund of the [JURISDICTION] of Columbia. All additional monies obtained pursuant to sections 6 and 9, and all interest earned on those funds, shall be deposited into the Fund without regard to fiscal year limitation pursuant to an act of Congress, and used solely to pay the costs of operating and maintaining the Fund and for the purposes stated in subsection (c) of this section. All funds, interest, and other amounts deposited into the Fund shall not be transferred or revert to the General Fund of the [JURISDICTION] of Columbia at the end of any fiscal year or at any other time, but shall continually be available for the uses and purposes set forth in this section, subject to authorization by Congress in an appropriations act.

(b) The [GOVERNING BODY] shall administer the monies deposited in the Fund.

(c) The Fund shall be used as follows:

- Staffing and operating costs to provide technical assistance, plan review, and inspections and monitoring of green buildings;

- Education, training and outreach to the public and private sectors on green building practices; and

- Incentive funding for private buildings as provided for in Section 7.

Section. 9. Green building fee.

- A green building fee is established to fund the implementation this ordinance and the Green Building Fund.

- Upon the effective date of this ordinance, the green building fee shall be established by increasing the building construction permit fees in effect at the time in accordance with the following schedule of additional fees:

- New construction – an additional $0.0020 per square foot.

- Alterations and repairs exceeding $1,000 but not exceeding $1 million – an additional 0.13 percent of construction value; and

- Alterations and repairs exceeding $1 million - an additional 0.065 percent of construction value.

Section. 10. Establishment of a [JURISDICTION] Green Building Advisory Council.

- The Department of the Environment shall provide the central coordination and technical assistance to [JURISDICTION] agencies and instrumentalities in the implementation of the provisions of this ordinance.

- Within 90 days after the effective date of this ordinance, the [GOVERNING BODY] shall establish a Green Building Advisory Council to monitor the [JURISDICTION]’s compliance with the requirements of this ordinance and to make policy recommendations designed to continually improve and update the ordinance.

- The [JURISDICTION] GBAC shall consist of the following nine (9) members: (1), (2), (3), (4), (5), (6), (7), (8), and (9).

  - Members of the GBAC who are not ex officio members shall have expertise in building construction, development, engineering, natural resources conservation, energy conservation, green building practices, environmental protection, environmental law, or other similar green building expertise.

  - The Chairperson of the GBAC shall be the Director of the Department of the Environment.

  - All members of the GBAC shall either work in, or be residents of the [JURISDICTION], and shall serve without compensation.

  - The members shall serve a 2-year term.

  - A member appointed to fill a vacancy or after a term has begun, shall serve only for the remainder of the term or until a successor is appointed.

  - The GBAC shall advise the [GOVERNING BODY] on:

    - The development, adoption, and revisions of this ordinance, including suggestions for additional incentives to promote green building practices;

    - The evaluation of the effectiveness of the [JURISDICTION]’s green building policies and their impact on the [JURISDICTION]’s environmental health, including the relation of the development of the [JURISDICTION]’s green building policies to the specific environmental challenges facing the [JURISDICTION];

    - The green building practices to be included in the triennial revisions of the Construction Codes; and

    - The promotion of green building education, including educating relevant [JURISDICTION] employees, the building community, and the public regarding the benefits and techniques of high-performance building standards.

    - The GBAC shall meet at least six (6) times each year.

  - The GBAC shall issue an annual report of its recommendations to the [GOVERNING BODY]. The report shall include recommended updates of green building standards, building systems monitoring and data compiled from [JURISDICTION]-owned or [JURISDICTION] instrumentality-owned and operated buildings, and an analysis of the building projects exempted by the [GOVERNING BODY] under section 11. The report shall be distributed to all members of the Council and the [GOVERNING BODY] and made available to the general public within 30 days after its issuance.

Section. 11. Exemptions and extensions. The [GOVERNING BODY] may, in unusual circumstances and only upon a showing of good cause, grant an exemption from any of the requirements of this ordinance based on:

- Substantial evidence of a practical infeasibility or hardship of meeting a required green building standard;

- A determination that the public interest would not be served by complying with such requirements; or

- Other compelling circumstances as determined by the [GOVERNING BODY] by rulemaking.

  - The burden shall be on the applicant to show circumstances to establish hardship or infeasibility under this section.

  - If the [GOVERNING BODY] determines that the required verification requirement is not practicable for a project, the [GOVERNING BODY] shall determine if another green building standard is practicable before exempting the project from all green building requirements.

  - The [GOVERNING BODY] shall promulgate rules to establish requirements for the exemption process within 180 days of the effective date of this ordinance.

- Notwithstanding any other provision of this ordinance, construction encompassed by building construction permits applied for within 180 days (6 months) of the effective date of this ordinance shall be exempt from the verification requirements of this ordinance.

- Notwithstanding any other provision of this ordinance, the [GOVERNING BODY], upon a finding of reasonable grounds, may extend the period for green building verifications required in Section 6(g) sub-parts (1) and (2), for up to three (3) successive 120-day (4-month) periods.

Section 12. Rulemaking. Within 180 days of the effective date of this ordinance, the [GOVERNING BODY] shall promulgate rules to implement this ordinance. The proposed rules shall be submitted to the [GOVERNING BODY] for a 45-day period of review, excluding Saturdays, Sundays, legal holidays, and days of [GOVERNING BODY] recess. If the [GOVERNING BODY] does not approve or disapprove the proposed rules, in whole or in part, by resolution within this 45-day review period, the proposed rules shall be deemed approved.

Section13. That the [JURISDICTION’S KEEPER OF RECORDS] is hereby ordered and directed to cause this ordinance to be published. (An additional provision may be required to direct the number of times the ordinance is to be published and to specify that it is to be in a newspaper in general circulation. Posting may also be required.)

Section 14. That this ordinance and the rules, regulations, provisions, requirements, orders and matters established and adopted hereby shall take effect and be in full force and effect [TIME PERIOD] from and after the date of its final passage and adoption.

APPENDIX B

GREENHOUSE GAS REDUCTION IN EXISTING BUILDINGS

The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.

SECTION B101

GENERAL

B101.1 Scope.  The provisions of this chapter are designed to reduce greenhouse gas emissions in existing buildings.

Exception:

- Phases 2 – 4 in Section B103 shall not be required for buildings with an initial certificate of occupancy less than 5 years old.

- Buildings that generate less than [jurisdiction to insert] pounds of CO2 per square foot., per year.

- Building owners that demonstrate to the code official that GHG emission reductions meeting the intent of this code have been accomplished prior to adoption of this appendix.

B101.2 Intent.  This chapter shall provide the basis and establish targets by which a jurisdiction can implement measures to reduce the emission of greenhouse gases in existing buildings.  This chapter further intends to provide a structure by which other features can be introduced into existing buildings for the purpose of making them more sustainable.

SECTION B102

DEFINITIONS

CARBON FOOTPRINT, BUILDING.  The total amount of carbon dioxide equivalent emissions associated with a building’s energy use.  A building’s carbon footprint is the sum of direct greenhouse gas emissions, indirect greenhouse gas emissions (for district energy), and indirect greenhouse gas emissions (for purchased electricity).  A building’s carbon footprint does not include energy use associated with vehicle travel unless accounted for in the building’s utility billing.

GHG REDUCTION PLAN.  A plan that identifies quantifiable measures for reducing greenhouse gas (GHG) emissions.  The plan shall include timelines for implementation, estimates of greenhouse gas reductions, and provisions for verifying actual greenhouse gas reductions – compared to original estimated reductions.

GREENHOUSE GAS INVENTORY.  A comprehensive quantification of greenhouse gas emissions associated with a building’s energy use limited to Scope 1 and Scope 2 greenhouse gases emitted from the use of primary and secondary energy.

SCOPE 1 GREENHOUSE GASES.  Direct greenhouse gas emissions from the combustion of non-renewable fuels on-site including, but not limited to, natural gas or oil.

SCOPE 2 GREENHOUSE GASES.  Greenhouse gas emissions resulting from the generation of electricity, heat, or steam purchased from sources off-site.

PRIMARY ENERGY.  The raw fuel that is burned to create heat and electricity, including, but not limited to, natural gas or fuel oil used in onsite generation.

SECONDARY ENERGY.  The energy product (heat or electricity) created from a raw fuel, such as electricity purchased from the grid or heat received from a district steam system.

SECTION B103

PHASES

B103.1  The adopting jurisdiction shall select Phase 1, 2, 3, or 4 as the level of compliance for application of this chapter.  Adoption of Phases 2, 3, or 4 requires that the lower phase(s) shall be applicable.

B103.2 Phase 1 .  Owners of buildings with a total building floor area greater than 5,000 square feet, and owners of individual spaces with an area greater than 5,000 square feet within multiple-tenant buildings, shall develop a greenhouse gas inventory to calculate the carbon footprint of their building or space within [JURISDICTION TO INSERT] months of adoption of this code by the jurisdiction as follows:

The carbon footprint shall be calculated using The Greenhouse Gas Protocol, A Corporate Accounting and Reporting Standard, Revised Edition developed by the World Resources Institute or other accepted industry practices protocols.  Energy data that was used to determine the carbon footprint of a building shall be made available to the jurisdiction by building owners.

Exception:  The omission of process loads from the carbon footprint calculations when provisions, such as separate metering, have been installed that make it possible to calculate process energy loads separately from a building’s operational energy loads, as approved by the code official.

B103.3 Phase 2.  Within [JURISDICTION TO INSERT] year(s) of performing the GHG inventory and calculating the carbon footprint identified in Phase 1, building owners shall develop a Greenhouse Gas Reduction Plan (Plan) to reduce GHG emissions by [JURISDICTION TO INSERT] percent.

B103.4 Phase 3.  Within X1 year(s) of developing the GHG Reduction Plan, building owners shall fully implement the p Plan.  Building owners shall submit semi-annual reports to the jurisdiction that identify progress being made towards fulfillment of the GHG Reduction Plan.

B103.5 Phase 4.  Building owners shall continue to reduce GHG emissions [JURISDICTION TO INSERT] percent per year (over the baseline year when the GHG Reduction Plan was first implemented) until total greenhouse gas emissions have been reduced by X percent.

SECTION B104

GREENHOUSE GAS REDUCTION METHODS

B104.1  Reduction in GHG’s can be achieved by any of the following methods:

- Implementation of building energy efficiency measures including, but not limited to, increasing insulation levels, installing higher efficient lighting and HVAC systems

- Installing renewable energy on the building or site

- Purchasing energy from renewable sources as approved by the jurisdiction. When energy purchased from renewable resources is used as a part of the GHG Reduction Plan, alternate provisions shall be included in the Plan that must be implemented when renewable energy purchases have ceased.

- Any other method approved by the jurisdiction that reduces the amount of greenhouse gases generated by the building’s operation, maintenance, and ongoing occupancy.

SECTION B105

REFERENCED STANDARDS

The Greenhouse Gas Protocol		 A Corporate Accounting and Reporting Standard		B103.2

Revised Edition developed by the World

Resources Institute……

APPENDIX C

SUSTAINABILITY MEASURES

The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.

SECTION C101

GENERAL

C101.1 Scope.  The provisions of this chapter are designed to increase the efficiency and sustainability of systems in existing buildings. These provisions apply to non residential buildings greater than 5000 square feet.

C101.2 Intent.  This chapter shall provide the basis by which a jurisdiction can implement measures to increase the water and energy efficiency, in existing buildings.  This chapter further intends to provide a structure by which other features can be introduced into existing buildings for the purpose of making them more sustainable.

SECTION C102

EFFICIENCY AND SUSTAINABILITY MEASURES

C102.1  Additional efficiency and sustainability measures within this section shall be incorporated into existing buildings within [JURISDICTION TO INSERT] months of adoption of this appendix.

C102.2  Energy performance.  Use one of the following four options to establish an acceptable level of energy use and measure energy efficiency performance:

Option 1: Receive an ENERGY STAR® rating of 75 or higher.

Option 2: Reduce energy use by [JURISDICTION TO INSERT] percent compared to building energy use in 2003 or a year thereafter with quality energy use data.

Option 3: Reduce energy use by [JURISDICTION TO INSERT] percent compared to the ASHRAE 90.1 2007 baseline building design if design information is available.

Option 4: Reduce energy use by [JURISDICTION TO INSERT] percent using an alternate metric approved by the code official.

Exception:  Adopting jurisdictions that do not have regulatory authority to establish energy efficiency standards are exempt from the provisions of Section B105.2.

C 102.3 Integrated assessment, operation, and management.  Use an integrated team to develop and implement policy regarding sustainable operations and maintenance including:

- Assess existing condition and operational procedures of the building and major building and systems and identify areas for improvement

- Establish operational performance goals for energy, water, material use and recycling, and indoor environmental quality, and ensure incorporation of these goals throughout the remaining lifecycle of the building.

- Incorporate a building management plan to ensure that operating decisions and tenant education are carried out with regard to integrated, sustainable building operations and maintenance

- Augment building operations and maintenance as needed using occupant feedback on work space satisfaction.

C102.4 Recommissioning.  A recommissioning plan shall be developed and implemented by an approved agency. The recommissioning shall be tailored to the size and complexity of the building and its system components in order to optimize and verify performance of fundamental building systems A final report documenting performance verification and correction of any discrepancies shall be filed with the jurisdiction upon request of the code official.

C 102.5 Water conservation.

C 102.5.1 Indoor water. One of the two following options shall be used to measure and reduce indoor potable water use:

Option 1: Reduce potable water use by 20 percent compared to a water baseline calculated for the building. The water baseline, for buildings with plumbing fixtures installed in 1994 or later, is 120 percent of the International Plumbing Code 2006 fixture performance requirements. The water baseline for plumbing fixtures older than 1994 is 160 percent of the International Plumbing Code 2006 fixture performance requirements, or;

Option 2: Reduce building measured potable water use by 20 percent compared to building water use in 2003 or a year thereafter with quality water data.

C102.5.2 Outdoor water. One of the three following options shall be used to measure and reduce outdoor potable water use:

Option 1: Reduce potable irrigation water use by 50 percent compared to conventional methods, or;

Option 2: Reduce building related potable irrigation water use by 50 percent compared to measured irrigation water use in 2003 or a year thereafter with quality water data, or;

Option 3: Use no potable irrigation water.

C102.5.3  Measurement of water use. Water meters for building sites with significant indoor and outdoor water use shall be used. If only one meter is installed, reduce potable water use (indoor and outdoor combined) by at least 20 percent compared to building water use in [year to be inserted by jurisdiction.]

C102.6 Indoor environmental quality enhancement.  The indoor environmental quality of buildings shall be improved in accordances with Sections C102.6.1 through C102.6.6.

C102.6.1  Ventilation and thermal comfort.  To the extent that is feasible, and as approved by the  code official, compliance with ASHRAE 55 and 62.1 shall be required.

C102.6.2  Moisture control.  A moisture control plan appropriate to the building shall be developed that includes measures to prevent building damage, minimize mold contamination, and reduce health risks related to moisture. For façade renovations, Dew Point analysis and a plan for cleanup or infiltration of moisture into building materials shall be included in the moisture control plan.

C102.6.3  Daylighting and lighting controls. Automated lighting controls including, but not limited to, occupancy and vacancy sensors with manual-off capability, shall be provided for appropriate spaces including, but not limited to, restrooms, conference, training, lunch, break and meeting rooms rooms and offices. Daylighting or occupant controlled lighting shall be provided in accordance with one of the following:

1: Achieve a minimum daylight factor of 2 percent (excluding all direct sunlight penetration) in 50 percent of all space occupied for critical visual tasks, or;

2: Provide occupant controlled lighting, allowing adjustments to suit individual task needs, for 50 percent of regularly occupied spaces.

C102.6.4  Low-emitting materials. A plan shall be developed specifiying the use of low VOC emitting materials for building modifications, maintenance, and cleaning. The plan shall specify the following materials and products to have low pollutant emissions: composite wood products, adhesives, sealants, interior paints and finishes, solvents, carpet systems, janitorial supplies, and furnishings.  Standards for low-emitting materials shall be as required in Chapter 8 of this code.

C102.6.5 Integrated pest management. Integrated pest management techniques shall be specified that are appropriate to the building and building site and minimize pesticide usage.

C102.6.6  Environmental tobacco smoke control. Smoking within the building and within 25 feet of all building entrances, operable windows, and building ventilation intakes shall be prohibited.

C102.7  Reduced material environmental impact.  The environmental impact of materials shall be reduced in accordance with this section.

C102.7.1  Waste and materials management. Where markets or on-site recycling exists, reuse and recycling services for building occupants shall be provided,. Salvage, reuse and recycling services for waste generated from building operations, maintenance, repair and minor renovations, and discarded furnishings, equipment and property shall be provided, including, but not limited to, beverage containers and paper from building occupants, batteries, toner cartridges, outdated computers from equipment updates and construction materials from a minor renovation.

C102.7.2  Ozone depleting compounds. The use of ozone depleting compounds shall be prohibited where alternative environmentally preferable products are available, consistent with either the Montreal Protocol and Title VI of the Clean Air Act Amendments of 1990, or equivalent overall air quality benefits that take into account lifecycle impacts.

SECTION C103

REFERENCED STANDARDS

ASHRAE 				Thermal Environmental Conditions on 				C102.6.1

55 – 2004				Human Occupancy

ASHRAE 				Ventilation for Acceptable Indoor Air Quality		C102.6.1

62.1 – 2010

ASHRAE

90.1 – 2010				Energy Standard for Buildings Except 				C102.2

Low-Rise Residential Buildings

EPA					Energy Star											C102.2

IPC 					International Plumbing Code 2012					C102.5.1

Montreal Protocol															C102.7.4

Clean Air Act		Title VI of Clean Air Act

1990 		Amendments of 1990…								C102.7.4

APPENDIX D

ENFORCEMENT PROCEDURES

The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.

D101

GENERAL

D101.1 Scope.  The provisions of this appendix shall supplement the provisions of Chapter 1 and provide procedures to enforce continued compliance of buildings, structures and building sites constructed and protected under the provisions of this code.

D101.2 Intent.  This appendix shall be construed to secure its expressed intent, which is to ensure public health, safety and welfare and protection of the environment insofar as they are affected by the continued occupancy and maintenance of buildings and building sites.  Existing buildings, structures and building site improvements that do not comply with these provisions shall be altered or repaired to restore compliance with this code.

D102

APPLICABILITY

D102.1 General.   Equipment, systems, devices, safeguards and protections required by this code or a previous code under which the building, structure or building site was constructed, altered or repaired; or under which portions of the building site were protected; shall be maintained.

D102.2 Owner responsibility. Except as otherwise specified in this code, the owner or the owner's designated agent shall be responsible for the maintenance of buildings, structures and building sites.  No owner, operator, or occupant shall cause any service, facility, equipment or utility that is required under this code to be removed or shut off from or discontinued.

D102.3 Existing remedies.  The provisions of this chapter shall not be construed to abolish or impair existing remedies of the jurisdiction or its officers or agencies relating to the removal or demolition of any structure or building site improvement that is dangerous, unsafe or causing irreparable harm to environmental systems.

D103

DEFINITIONS

D103.1 Definitions.  The following words and terms shall, for the purposes of this chapter and used elsewhere in this code, have the meanings shown herein.

OWNER.  Any person, agent, operator, firm or corporation having a legal or equitable interest in a building site; or recorded in the official records of the state, county or municipality as holding title to the building site; or otherwise having control of the building site, including the guardian of an estate of any person, and the executor or administrator of the estate of such person if ordered to take possession of real property by a court.

OPERATOR.  Any person who has charge, care or control of a building, structure and building site that is let or offered for occupancy.

STRICT LIABILITY OFFENSE.  An offense in which the prosecution in a legal proceeding is not required to prove criminal intent as a part of its case.  It is enough to prove that the defendant either did an act that is prohibited, or failed to do an act that the defendant was legally required to do.

D104

DUTIES AND POWERS OF THE CODE OFFICIAL

D104.1 General.  The code official is hereby authorized and directed to enforce the provisions of this chapter.

D104.2 Inspections.  The code official is authorized to make all inspections necessary for administration of this chapter, to assure compliance with maintenance requirements of this code and to resolve identified violations.

D104.3 Right of entry.  Where it is necessary to make an inspection to enforce the provisions of this code, or whenever the code official has reasonable cause to believe there exists in a building or structure or on a building site a condition in violation of the code, the code official is authorized to enter the building site, and if needed to enter the building or structure at reasonable times to inspect or perform the duties imposed by this code.  Where the building site or building is occupied, the code official shall present identification credentials to the occupant and request entry. If the building site or building is unoccupied, the code official shall first make a reasonable effort to locate the owner or other person having charge or control of the building site or building and request entry.  If entry is refused, the code official shall have recourse to the remedies provided by law to secure entry.

D104.4 Identification.  The code official shall carry proper identification credentials when inspecting a building or building site in the performance of duties under this code.

D104.5 Notices and orders.  The code official shall issue all necessary notices or orders to ensure compliance with this code.

D105

VIOLATIONS

D105.1 Unlawful acts.  It shall be unlawful for an owner or an owner's designated agent to be in conflict with, or violation of, any of the provisions of this code.

D105.2 Notice of violation.  The code official shall serve notice of the violation or issue an order in accordance with Section D106.

D105.3 Prosecution of violation.  Any person failing to comply with a notice of violation or order served in accordance with Section D106 shall be deemed guilty of a misdemeanor or civil infraction as determined by the jurisdiction, and the violation shall be deemed a strict liability offense.  If the notice of violation or order is not complied with, the code official shall institute the appropriate preceding at law or in equity to restrain, correct or abate the violation.  The expenses incurred by the jurisdiction during action taken by the jurisdiction on the building site or in the building shall be charged against the real estate of the building site and shall be a lien upon such real estate.

D105.4 Violation penalties.  Any person who violates the provisions of this code, or fails to comply with the provisions of this code, shall be prosecuted within the limits provided by the laws of the state and jurisdiction.  Each day that a violation continues after notice has been served in accordance with Section D106 shall be deemed a separate violation and offense.

D105.5 Abatement of violation.  The imposition of penalties under the provisions of this code shall not preclude  the legal officer of the jurisdiction from instituting appropriate  action to restrain, correct or abate a violation, or to prevent illegal occupancy of a building, structure or building site, or to stop an illegal act, conduct, business or utilization of a building, structure or building site.

D106

NOTICES AND ORDERS

D106.1 Notice of violation.  Whenever the code official determines that there has been a violation of this code or has grounds to believe that a violation has occurred, notice shall be given in the form and manner prescribed in Sections D106.2 and D106.3.

D106.2 Form of notice.  A notice of violation prescribed in Section D106.1 shall be in accordance with the following:

1. 	Be in writing;

2. 	Include a real estate description of the building site sufficient for identification;

3. 	Include a statement of the violation or violations and why the notice is being issued;

4. 	Include a correction order allowing a reasonable time to make repairs and improvements required to bring the building, structure and building site into compliance with the provisions of this code;

5.  	Inform the property owner and those receiving the notice and order of the right to appeal; and

6.  	Include a statement of the right of the jurisdiction to file a lien in accordance with Section D105.3.

D106.3 Service.  A notice of violation and order to comply shall be served in accordance with Sections D106.3.1 and D106.3.2.

D106.3.1 Recipient of notice.  The notice of violation and order to comply shall be served on the person responsible for the violation of the code.  When the person responsible for the violation is someone other than the owner of the building and building site, a copy of the notice shall also be served on the property owner.

D106.3.2 Method of service.  Such notice and order to comply shall be deemed to be properly served if a copy is:

1. 	Delivered personally; or

2. 	Sent by certified or first-class mail addressed to the last known address.

If a notice served by mail is returned showing that the letter was not delivered, a copy of the notice and order shall be posted in a conspicuous place in or about the building, structure or building site affected by the notice.

D106.4 Unauthorized tampering.  Notices, orders, signs, tags or seals posted or affixed by the code official shall not be mutilated, destroyed or tampered with, or removed without authorization from the code official.

D106.5 Penalties.  Penalties for noncompliance with notices and orders shall be as set forth in Section D105.4.

D106.6 Transfer of ownership.  It shall be unlawful of the owner of any building, structure or building site who has received a compliance order or upon whom a notice of violation has been served, to sell, transfer, mortgage, lease or otherwise dispose of the building, structure or building site to another until the provisions of the compliance order or notice of violation have been complied with, or until such owner shall first furnish the grantee, transferee, mortgagee or lessee a true copy of any compliance order or notice of violation issued by the code official and shall furnish to the code official a signed and notarized statement from the grantee, transferee, mortgagee or lessee, acknowledging the receipt of such compliance order or notice of violation and fully accepting the responsibility without condition for making corrections or repairs required by such compliance order or notice of violation.

D107

EMERGENCY MEASURES AND ABATEMENT

D107.1 Imminent hazard.  When, in the opinion of the code official, there is an imminent hazard to the building site or to surrounding public and private property resulting from the failure of a building or building site system, including but not limited to: stormwater management systems; erosion control measures; graywater or rainwater collection systems;  or dry vegetation used for vegetative roofs or hardscape shading;  which endangers life or which will cause irreparable harm to environmental systems on, or adjacent to, the building site, the code official is hereby authorized and empowered to order immediate repair of these systems and measures to restore proper operation.

D107.2 Temporary safeguards.  Notwithstanding other provisions of this code, whenever, in the opinion of the code official, there is an imminent hazard due to the failures of systems and measures, the code official shall order the necessary work done, whether or not the legal procedures specified in this chapter has been instituted; and shall cause such other action to be taken as the code official deems necessary to resolve the hazard.

D107.3 Closing streets. When necessary for public safety, the code official shall temporarily close or order the authority having jurisdiction to close sidewalks, streets, public ways and bicycle pathways, adjacent to the hazardous location.

D107.4 Emergency repairs.  For the purposes of this section, the code official shall employ the necessary labor and materials to perform the required work as expeditiously as possible.

D107.5 Costs of emergency repairs.  Costs incurred in the performance of the emergency work shall be paid by the jurisdiction.  The legal counsel of the jurisdiction shall institute appropriate action against the owner of the building site for the recovery of the costs.

D107.6 Hearing.  Any person ordered to take emergency measures shall comply with such order forthwith.  Any person affected thereafter, upon application to the board of violation appeals shall be afforded a hearing as described in this code.

D108

MEANS OF APPEAL

D108.1 General.  In order to hear and decide appeals of notices of violation and orders of compliance issued by the code official pursuant to this chapter, there shall be and hereby created a board of violation appeals.  Where the board of appeals established under Section 108 is in compliance with the provisions of Sections D108.1 through D108.6, the board of appeals shall be permitted to serve as the board of violation appeals.

D108.2 Board of violation appeals.  The board of violation appeals shall be appointed by the applicable governing authority and shall hold office at its pleasure.

D108.2.1 Membership of the board.  The board of violation appeals shall consist of a minimum of three members who are qualified by experience and training to pass on matters regulated by this code.  Members shall be appointed to serve staggered and overlapping terms.  Members of the board shall not be employees of the jurisdiction.  The code official shall be an ex-officio member but shall have no vote on any matter before the board.

D108.2.2 Alternate members.  The governing authority shall appoint two or more alternate members who shall be called by the chair of the board to hear appeals during the absence or disqualification of a member.  Alternate members shall possess the qualifications required for board membership.

D108.2.3 Board chair.  The board shall annually select one of its members to serve as chair.

D108.2.4 Disqualification of member.  A member shall not hear an appeal in which that member has a personal, professional or financial interest.

D108.2.5 Secretary.  The code official shall designate a qualified person to serve as secretary to the board.  The secretary shall file a detailed record of all proceedings in the office of the code official.

D108.3 Application for appeal.  Any person receiving a notice of violation issued by the code official pursuant to this chapter, shall have the right to appeal to the board of violation appeals.  The application for appeal shall be in writing and filed within 20 days after the day the notice of violation was served.  An application for appeal shall be based on a claim that the requirements of this code are adequately satisfied.

D108.4 Stays of enforcement.  Other than notices of imminent hazard, appeals of notices and orders shall stay the enforcement of the notice and order until the appeal is heard by the board of violation appeals.

D108.5 Hearing.  Hearings of appeals shall be in accordance with Sections D108.5.1 through D108.5.5.

D108.5.1 Notice.  The board shall meet upon notice from the chair, within 20 days of the filing of an appeal, or at stated periodic meetings.  Notice of the board meeting shall be published in the newspaper of record for the jurisdiction.  Written notice shall be provided to the owner of the building site subject to the notice of violation as well as any person cited in the notice of violation.

D108.5.2 Open hearing.  All hearings before the board shall be open to the public.  The appellant, the appellant's representative, the code official and any person whose interests are affected shall be given an opportunity to be heard.

D108.5.3 Quorum.  A quorum shall consist of not less than two-thirds of the board membership.  A quorum shall be present in order for a hearing to proceed.

D108.5.4 Hearing procedures.  The board shall adopt and make available to the public through the secretary procedures under which a hearing will be conducted.  The procedures shall not require compliance under strict rules of evidence, but shall mandate that only relevant information be received.

D108.5.5 Postponement of hearing.  When the full board is not present to hear an appeal, either the appellant or the appellant's representative shall have the right to request postponement of the hearing.

D108.6 Board decision. The board of violations appeal shall either uphold, modify or reverse the decision of the code official.  The board shall modify or reverse the decision of the code official only by a concurring vote of a majority of the total number of appointed board members.  The decision of the board to uphold, modify or reverse the decision of the code official shall be in writing and shall direct actions appropriate to implement the decision.

D108.6.1 Records and copies.  The decision and directive of the board shall be recorded.  Copies shall be furnished to the appellant, the owner of the building site and to the code official.

D108.6.2 Implementation.  The code official shall take immediate action in accordance with the decision of the board.

D108.7 Court review.  Any person, whether or not a previous party of the appeal, shall have the right to apply to the appropriate court for a writ of certiorari to correct errors of law.  Application for review shall be made in the manner and time required by law.

NOTES

# Text boxes

% CLAY

AHRI

APHA

ARB

ASA

ASME

ASHRAE

ASSE

ASTM

CCR

CRRC

CSA

DCHS

DOC

DOE

EPA

IEC

ICC

IESNAAA

ISO

NREL

NFPA

NSF

SCAQMD

SFI

SMACNA

TMS

UL

USCC

USDA